## 153_234
S&C Power Fuses - Type SMU-40 (14.4 and 25 kV) | [9 empty] | S&C Power Fuses - Type SMU-40 (14.4 and 25 kV) | [9 empty] | S&C Power Fuses - Type SMU-40 (14.4 and 25 kV) | [9 empty] | S&C Power Fuses - Type SMU-40 (14.4 and 25 kV) | [9 empty] | S&C Power Fuses - Type SMU-40 (14.4 and 25 kV)
Standard Speed (TCC 153-2-3-4) | [9 empty] | Standard Speed (TCC 153-2-3-4) | [9 empty] | Standard Speed (TCC 153-2-3-4) | [9 empty] | Standard Speed (TCC 153-2-3-4) | [9 empty] | Standard Speed (TCC 153-2-3-4)
Total Clearing Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated June 17, 1991
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
3E |  | 5E |  | 7E |  | 10E |  | 13E |  | 15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 400E |  | 2-250E |  | 2-300E |  | 2-400E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
29999.2 | 0.015204 | 29999.2 | 0.015204 | 29999.2 | 0.015204 | 29999.2 | 0.015204 | 29999.2 | 0.015204 | 29999.2 | 0.015204 | 29999.2 | 0.015296 | 29999.2 | 0.015296 | 29999.2 | 0.015296 | 29999.2 | 0.015296 | 29999.2 | 0.015296 | 29999.2 | 0.015403 | 29999.2 | 0.015403 | 29999.2 | 0.015605 | 29999.2 | 0.018701 | 29999.2 | 0.019003 | 29999.2 | 0.019213 | 29999.2 | 0.019406 | 29999.2 | 0.019997 | 29999.2 | 0.022412 | 29999.2 | 0.024109 | 29999.2 | 0.026698 | 29999.2 | 0.030313 | 29999.2 | 0.036803
23504 | 0.017092 | 25872.2 | 0.016405 | 28621.8 | 0.015605 | 28593.2 | 0.015605 | 28422.2 | 0.015605 | 25032.4 | 0.016603 | 26527.2 | 0.016209 | 26132.2 | 0.016307 | 28822.9 | 0.015605 | 28479.1 | 0.015699 | 26713.5 | 0.016209 | 28111.3 | 0.015904 | 27389.8 | 0.016209 | 26158.4 | 0.016703 | 25309.2 | 0.020689 | 24414.3 | 0.021598 | 27417.2 | 0.020401 | 23015.5 | 0.023094 | 27554.6 | 0.021107 | 26054 | 0.0256 | 25640.4 | 0.028292 | 28167.5 | 0.028691 | 27971 | 0.033003 | 27859.4 | 0.040715
18086.6 | 0.019503 | 19909 | 0.018608 | 22002.8 | 0.0177 | 21980.8 | 0.0177 | 21871.2 | 0.017789 | 19262.7 | 0.018908 | 20392.6 | 0.018404 | 20109 | 0.018497 | 22179.5 | 0.0177 | 21915 | 0.017789 | 20535.8 | 0.018497 | 21631.9 | 0.018094 | 21055.7 | 0.018497 | 20129.2 | 0.019213 | 19475.7 | 0.024303 | 18768.3 | 0.0256 | 21076.7 | 0.024206 | 17710.7 | 0.027788 | 21203.6 | 0.025498 | 20048.8 | 0.033003 | 19710.9 | 0.037509 | 26633.5 | 0.030587 | 24832.9 | 0.038305 | 26210.8 | 0.044415
13903.9 | 0.0221 | 15304.8 | 0.021107 | 16931.4 | 0.020097 | 16914.5 | 0.020097 | 16830.1 | 0.020198 | 14808 | 0.021511 | 15692.3 | 0.020897 | 15474.1 | 0.021107 | 17067.4 | 0.020097 | 16846.9 | 0.020299 | 15802.5 | 0.021001 | 16629.4 | 0.020689 | 16202.6 | 0.021297 | 15489.6 | 0.022211 | 14971.8 | 0.028691 | 14442.4 | 0.030679 | 16218.8 | 0.029008 | 13628.6 | 0.034008 | 16316.4 | 0.031299 | 15412.4 | 0.043276 | 19128.3 | 0.03869 | 25082.5 | 0.032707 | 21871.2 | 0.045222 | 24463.2 | 0.048989
10699.2 | 0.025093 | 11777.2 | 0.023989 | 13028.9 | 0.022796 | 13015.9 | 0.022887 | 12938 | 0.022887 | 11394.9 | 0.0244 | 12075.4 | 0.023798 | 11895.6 | 0.023989 | 13120.4 | 0.022887 | 12963.9 | 0.023094 | 12148.1 | 0.023989 | 12796.5 | 0.023703 | 12468 | 0.024498 | 11907.5 | 0.025909 | 11521 | 0.034315 | 11113.6 | 0.037285 | 12480.5 | 0.035431 | 10476.9 | 0.042376 | 12543.1 | 0.039393 | 14956.8 | 0.044683 | 18213.6 | 0.040919 | 22809.3 | 0.03651 | 19339.9 | 0.053281 | 22537.3 | 0.055014
8233.18 | 0.028491 | 9062.75 | 0.027183 | 10015.8 | 0.025909 | 10005.8 | 0.026013 | 9955.97 | 0.026117 | 8768.56 | 0.027704 | 9282.89 | 0.026993 | 9153.83 | 0.027292 | 10096.3 | 0.026117 | 9965.93 | 0.026406 | 9348.1 | 0.027484 | 9847.06 | 0.027401 | 9584.74 | 0.028491 | 9162.99 | 0.030618 | 8865.55 | 0.041371 | 8543.52 | 0.046228 | 9594.33 | 0.044018 | 10045.9 | 0.044106 | 11406.3 | 0.042888 | 13987.6 | 0.048067 | 17118.7 | 0.043886 | 20250.3 | 0.042207 | 16999.3 | 0.063917 | 21118.9 | 0.060497
6329.19 | 0.032382 | 6966.92 | 0.030895 | 7707.34 | 0.029506 | 7699.63 | 0.029506 | 7661.23 | 0.029594 | 6740.76 | 0.031487 | 7143.29 | 0.030771 | 7036.94 | 0.031174 | 7761.48 | 0.029802 | 7668.9 | 0.030223 | 7193.46 | 0.031677 | 7569.85 | 0.031804 | 7375.57 | 0.033602 | 7051.02 | 0.036583 | 6815.32 | 0.050988 | 8332.58 | 0.047209 | 9357.45 | 0.044997 | 9320.09 | 0.047398 | 10126.6 | 0.048259 | 12418.3 | 0.054904 | 16332.7 | 0.046321 | 17290.7 | 0.051295 | 15001.8 | 0.076599 | 19671.5 | 0.067194
4870.38 | 0.036803 | 5361.12 | 0.035114 | 5924.95 | 0.033501 | 5924.95 | 0.033501 | 5889.51 | 0.033703 | 5187.09 | 0.035895 | 5491.34 | 0.035114 | 5415 | 0.035609 | 5972.54 | 0.034008 | 5901.3 | 0.034695 | 5529.92 | 0.036583 | 5825.08 | 0.03721 | 5675.58 | 0.040108 | 5420.42 | 0.044907 | 6713.85 | 0.051707 | 7784.8 | 0.050078 | 9126.41 | 0.04609 | 8569.19 | 0.051192 | 8646.66 | 0.05686 | 10937.2 | 0.063598 | 15505.1 | 0.049185 | 15122.3 | 0.061288 | 13425.7 | 0.09007 | 18213.6 | 0.075384
3744.07 | 0.041662 | 4121.32 | 0.039908 | 4559.32 | 0.038 | 4554.76 | 0.038114 | 4532.04 | 0.038305 | 3987.53 | 0.040919 | 4225.65 | 0.040108 | 4166.9 | 0.040919 | 4595.94 | 0.039001 | 4536.58 | 0.040108 | 4255.33 | 0.042674 | 4482.46 | 0.044194 | 4363.06 | 0.048793 | 5339.72 | 0.045494 | 6463.51 | 0.053335 | 7229.52 | 0.053602 | 8803.71 | 0.047541 | 7792.59 | 0.056294 | 7562.28 | 0.066194 | 9671.4 | 0.073522 | 14763.7 | 0.052226 | 12681.8 | 0.077835 | 11671.7 | 0.1119 | 16897.6 | 0.084825
2881.1 | 0.047398 | 3171.4 | 0.045313 | 3508.45 | 0.043189 | 3504.94 | 0.043406 | 3483.97 | 0.04358 | 3068.45 | 0.046693 | 3251.68 | 0.045906 | 3203.27 | 0.047115 | 3533.09 | 0.044997 | 3490.95 | 0.046693 | 3274.53 | 0.050481 | 3445.86 | 0.053495 | 4306.7 | 0.049283 | 5202.68 | 0.046506 | 6062.81 | 0.05635 | 6680.37 | 0.057777 | 8458.51 | 0.049283 | 7086.37 | 0.062339 | 6341.86 | 0.081744 | 8500.91 | 0.086279 | 13931.7 | 0.055901 | 11135.8 | 0.093465 | 10351.9 | 0.13518 | 15802.5 | 0.094216
2217.04 | 0.053817 | 2440.43 | 0.0515 | 2697.09 | 0.049185 | 2694.39 | 0.049382 | 2680.95 | 0.049779 | 2361.21 | 0.053388 | 2499.71 | 0.052804 | 2464.95 | 0.05463 | 2718.75 | 0.052226 | 2686.32 | 0.055014 | 2517.26 | 0.060618 | 3397.95 | 0.054033 | 4179.42 | 0.050481 | 5028.76 | 0.047923 | 5704.03 | 0.059477 | 6172.93 | 0.062401 | 8134.98 | 0.05109 | 6405.6 | 0.06931 | 5568.76 | 0.096312 | 7502.02 | 0.10125 | 13107.3 | 0.060315 | 9442.05 | 0.11929 | 8681.31 | 0.17958 | 14587.6 | 0.10697
1704.33 | 0.061105 | 1876.06 | 0.058591 | 2075.44 | 0.055957 | 2073.36 | 0.056294 | 2063.02 | 0.05686 | 1815.16 | 0.061288 | 1923.55 | 0.061105 | 1896.81 | 0.064045 | 2092.11 | 0.061288 | 2065.09 | 0.065667 | 2487.24 | 0.061227 | 3277.8 | 0.055511 | 3896.87 | 0.053495 | 4788.29 | 0.049978 | 5409.59 | 0.062526 | 5568.76 | 0.069102 | 7761.48 | 0.053495 | 5813.44 | 0.077447 | 4721.72 | 0.12049 | 6713.85 | 0.11717 | 12233.4 | 0.065798 | 8086.31 | 0.1512 | 7615.4 | 0.22265 | 13683.2 | 0.11834
1311.5 | 0.069379 | 1443.65 | 0.066659 | 1597.07 | 0.063853 | 1595.48 | 0.064302 | 1585.93 | 0.065274 | 1396.78 | 0.070781 | 1480.19 | 0.071421 | 1458.16 | 0.075837 | 1608.29 | 0.072791 | 2034.34 | 0.066393 | 2428.25 | 0.062339 | 3161.9 | 0.057202 | 3582.9 | 0.057489 | 4554.76 | 0.052226 | 5008.68 | 0.067194 | 5150.91 | 0.075008 | 7464.61 | 0.055623 | 5233.99 | 0.087583 | 4043.75 | 0.1506 | 5836.74 | 0.14183 | 11270.3 | 0.072937 | 6946.05 | 0.19202 | 6707.14 | 0.27744 | 12719.9 | 0.1341
1009.21 | 0.078853 | 1110.9 | 0.075837 | 1227.74 | 0.072937 | 1226.51 | 0.073743 | 1220.39 | 0.075233 | 1074.84 | 0.082318 | 1137.89 | 0.084318 | 1425 | 0.076983 | 1579.6 | 0.073817 | 1978.17 | 0.067802 | 2351.78 | 0.063853 | 3037.92 | 0.059003 | 3327.34 | 0.061411 | 4166.9 | 0.056576 | 4702.87 | 0.071421 | 4783.5 | 0.081336 | 7058.08 | 0.058709 | 4735.91 | 0.099245 | 3473.54 | 0.18897 | 5176.73 | 0.16811 | 10561 | 0.079407 | 6111.5 | 0.23665 | 5924.95 | 0.34502 | 12039.2 | 0.14585
775.828 | 0.089531 | 854 | 0.086625 | 944.76 | 0.083395 | 943.816 | 0.08491 | 939.108 | 0.087496 | 826.278 | 0.096794 | 1110.9 | 0.085763 | 1344.7 | 0.080205 | 1535.99 | 0.075233 | 1896.81 | 0.069797 | 2266.35 | 0.065601 | 2924.64 | 0.060922 | 3065.38 | 0.06626 | 3889.08 | 0.060497 | 4384.93 | 0.07637 | 4336.96 | 0.091066 | 6754.26 | 0.061411 | 4187.79 | 0.11635 | 3056.2 | 0.23127 | 4341.3 | 0.21737 | 9837.21 | 0.087234 | 5265.48 | 0.30662 | 5120.09 | 0.44568 | 11147 | 0.16727
597.008 | 0.10176 | 657.162 | 0.099047 | 726.277 | 0.095927 | 726.277 | 0.098356 | 721.932 | 0.10257 | 813.976 | 0.097767 | 1075.91 | 0.087583 | 1266.39 | 0.083897 | 1477.24 | 0.077292 | 1813.34 | 0.072283 | 2181.85 | 0.067599 | 2710.61 | 0.064883 | 2795.95 | 0.0725 | 3586.49 | 0.06547 | 4035.67 | 0.083395 | 3936.03 | 0.10196 | 6412.01 | 0.064754 | 3796.85 | 0.1329 | 2633.13 | 0.29815 | 3808.26 | 0.2647 | 9108.18 | 0.096601 | 4660.73 | 0.38668 | 4509.44 | 0.566 | 10487.3 | 0.18634
459.405 | 0.11588 | 505.188 | 0.11359 | 558.878 | 0.11078 | 558.319 | 0.11496 | 711.895 | 0.10361 | 787.553 | 0.099842 | 1042.03 | 0.089353 | 1158.55 | 0.089442 | 1405.19 | 0.080205 | 1714.59 | 0.075384 | 2081.67 | 0.070217 | 2524.83 | 0.069102 | 2601.72 | 0.077757 | 3337.34 | 0.070498 | 3695.71 | 0.091615 | 3582.9 | 0.1145 | 6099.29 | 0.068415 | 3438.97 | 0.15287 | 2330.71 | 0.37525 | 3354.06 | 0.32395 | 8450.05 | 0.1073 | 4158.58 | 0.48765 | 4121.32 | 0.68307 | 9926.15 | 0.20533
353.164 | 0.13171 | 388.748 | 0.13092 | 430.063 | 0.1291 | 545.079 | 0.11658 | 685.351 | 0.10602 | 755.917 | 0.10257 | 998.177 | 0.092166 | 1078.07 | 0.094594 | 1316.76 | 0.084149 | 1598.67 | 0.079726 | 1958.49 | 0.073743 | 2337.71 | 0.074039 | 2442.87 | 0.083228 | 3016.73 | 0.078696 | 3184.11 | 0.10837 | 3216.11 | 0.13145 | 5761.36 | 0.072791 | 3168.23 | 0.17202 | 2079.59 | 0.47276 | 2962.91 | 0.39607 | 7902.45 | 0.11787 | 3673.6 | 0.64265 | 3819.7 | 0.81045 | 9135.54 | 0.23951
271.763 | 0.14999 | 299.146 | 0.15211 | 420.284 | 0.13092 | 526.858 | 0.11906 | 665.096 | 0.10816 | 719.769 | 0.10612 | 944.76 | 0.095831 | 987.257 | 0.10125 | 1232.66 | 0.088463 | 1427.85 | 0.087321 | 1853.68 | 0.07706 | 2106.81 | 0.08158 | 2291.42 | 0.089085 | 2759.84 | 0.087146 | 2832.54 | 0.12466 | 2904.24 | 0.1506 | 5491.34 | 0.076676 | 2910.06 | 0.19492 | 1837.07 | 0.62365 | 2560.42 | 0.503 | 7294.88 | 0.13224 | 3304.13 | 0.8227 | 3526.03 | 0.98102 | 8374.34 | 0.28248
208.916 | 0.17082 | 294.398 | 0.15348 | 403.401 | 0.13423 | 508.737 | 0.1217 | 641.578 | 0.11067 | 674.473 | 0.11078 | 895.096 | 0.099742 | 912.265 | 0.10794 | 1145.88 | 0.09384 | 1303.65 | 0.094594 | 1733.55 | 0.081744 | 1927.4 | 0.089263 | 2136.51 | 0.096312 | 2469.89 | 0.099146 | 2547.65 | 0.14211 | 2545.11 | 0.18102 | 5228.75 | 0.08093 | 2667.58 | 0.22287 | 1652.31 | 0.79999 | 2255.05 | 0.62929 | 6842.63 | 0.14483 | 2998.68 | 1.0638 | 3350.71 | 1.1228 | 7691.94 | 0.3365
160.763 | 0.19512 | 284.556 | 0.15658 | 381.431 | 0.13888 | 491.239 | 0.12454 | 612.734 | 0.11416 | 616.422 | 0.11799 | 842.127 | 0.10412 | 845.502 | 0.11519 | 1058.84 | 0.099942 | 1198.62 | 0.10196 | 1645.71 | 0.085592 | 1730.09 | 0.099942 | 1964.37 | 0.10612 | 2273.16 | 0.11012 | 2314.45 | 0.16119 | 2261.83 | 0.21521 | 4958.85 | 0.086279 | 2392.1 | 0.26417 | 1499.56 | 1.0375 | 2060.96 | 0.75114 | 6360.92 | 0.16216 | 2729.65 | 1.3894 | 3158.74 | 1.3032 | 7121.89 | 0.39567
123.709 | 0.22354 | 275.044 | 0.15975 | 360.298 | 0.14382 | 452.565 | 0.13118 | 580.524 | 0.11822 | 573.026 | 0.12454 | 784.409 | 0.11001 | 779.717 | 0.12379 | 988.245 | 0.10602 | 1110.9 | 0.10957 | 1532.92 | 0.091158 | 1559.2 | 0.11212 | 1795.3 | 0.11799 | 2046.59 | 0.12579 | 2138.65 | 0.17975 | 2046.59 | 0.24928 | 4707.58 | 0.091523 | 2194.98 | 0.30387 | 1365.02 | 1.3591 | 1910.13 | 0.88324 | 6020.52 | 0.17532 | 2547.65 | 1.7243 | 2962.91 | 1.5509 | 6405.6 | 0.497
95.1004 | 0.25713 | 263.204 | 0.16395 | 336.276 | 0.15044 | 418.188 | 0.13846 | 549.457 | 0.12293 | 535.891 | 0.13105 | 728.459 | 0.1167 | 708.345 | 0.13558 | 904.996 | 0.1145 | 1019.36 | 0.11918 | 1461.07 | 0.095544 | 1427.85 | 0.12404 | 1670.58 | 0.12936 | 1879.81 | 0.14083 | 1990.08 | 0.19826 | 1859.25 | 0.28905 | 4469.04 | 0.097572 | 2000.05 | 0.35481 | 1274.01 | 1.6902 | 1763.27 | 1.0585 | 5574.33 | 0.19846 | 2340.05 | 2.3487 | 2746.08 | 1.9325 | 5942.76 | 0.58675
92.9381 | 0.2605 | 247.629 | 0.17031 | 299.146 | 0.16265 | 386.036 | 0.14614 | 507.213 | 0.13001 | 492.715 | 0.13971 | 674.473 | 0.12404 | 655.849 | 0.14571 | 830.419 | 0.12404 | 932.557 | 0.13053 | 1391.21 | 0.10024 | 1308.88 | 0.13819 | 1565.45 | 0.14055 | 1719.74 | 0.15943 | 1864.83 | 0.21802 | 1685.69 | 0.33717 | 4251.08 | 0.10361 | 1833.4 | 0.4143 | 1170.2 | 2.3091 | 1675.6 | 1.203 | 5244.46 | 0.21911 | 2188.4 | 3.0952 | 2570.69 | 2.3865 | 5607.88 | 0.67425
89.0265 | 0.26682 | 235.316 | 0.17584 | 268.522 | 0.17532 | 351.402 | 0.15643 | 471.506 | 0.13708 | 447.167 | 0.1512 | 634.559 | 0.13079 | 606.031 | 0.15784 | 753.652 | 0.13613 | 856.566 | 0.14296 | 1322.03 | 0.10538 | 1196.23 | 0.15472 | 1425 | 0.15911 | 1578.02 | 0.18066 | 1721.46 | 0.24484 | 1471.34 | 0.42225 | 4011.53 | 0.11156 | 1733.55 | 0.45696 | 1094.36 | 3.0552 | 1579.6 | 1.388 | 4963.81 | 0.23951 | 2052.73 | 4.178 | 2428.25 | 2.912 | 5286.59 | 0.77557
83.9259 | 0.27578 | 219.408 | 0.18375 | 237.444 | 0.19163 | 317.962 | 0.16844 | 440.069 | 0.1444 | 398.988 | 0.16643 | 595.816 | 0.13791 | 540.736 | 0.17797 | 686.723 | 0.14969 | 778.938 | 0.15879 | 1240.07 | 0.11257 | 1093.27 | 0.17444 | 1315.44 | 0.17779 | 1425 | 0.21052 | 1608.29 | 0.2714 | 1326.01 | 0.5035 | 3793.06 | 0.12001 | 1632.6 | 0.51265 | 1026.52 | 4.1323 | 1481.67 | 1.6386 | 4568.45 | 0.27605 | 1976.19 | 5.2375 | 2340.05 | 3.3866 | 5053.96 | 0.8727
79.4346 | 0.28418 | 205.189 | 0.19163 | 212.285 | 0.20864 | 289.146 | 0.18156 | 398.589 | 0.15596 | 353.871 | 0.18504 | 551.66 | 0.14761 | 494.195 | 0.19708 | 641.578 | 0.16071 | 712.608 | 0.17619 | 1180.78 | 0.11834 | 952.348 | 0.21052 | 1211.88 | 0.19886 | 1301.05 | 0.2424 | 1481.67 | 0.30784 | 1176.06 | 0.62241 | 3590.07 | 0.1291 | 1557.64 | 0.56093 | 988.245 | 5.1906 | 1373.24 | 2.0255 | 4187.79 | 0.32169 | 1893.02 | 7.0487 | 2237.08 | 4.2838 | 4802.67 | 0.99784
74.2126 | 0.29518 | 190.363 | 0.20146 | 187.341 | 0.23058 | 263.995 | 0.19531 | 365.743 | 0.16743 | 315.428 | 0.20697 | 497.17 | 0.16281 | 453.925 | 0.21693 | 600.001 | 0.17288 | 642.22 | 0.20006 | 1117.59 | 0.12566 | 867.774 | 0.24095 | 1097.65 | 0.22943 | 1198.62 | 0.27688 | 1392.6 | 0.33886 | 1066.27 | 0.74889 | 3394.56 | 0.1393 | 1484.64 | 0.61868 | 946.651 | 6.9925 | 1285.53 | 2.4839 | 3846.54 | 0.37826 | 1840.75 | 9.5338 | 2145.07 | 5.5836 | 4513.95 | 1.1887
68.7127 | 0.30846 | 176.431 | 0.21221 | 170.193 | 0.25003 | 240.791 | 0.21116 | 330.607 | 0.18247 | 283.137 | 0.23081 | 460.324 | 0.17549 | 421.126 | 0.23784 | 547.811 | 0.19183 | 583.434 | 0.22646 | 1049.35 | 0.13518 | 791.501 | 0.27633 | 977.434 | 0.27385 | 1128.82 | 0.30509 | 1298.45 | 0.37864 | 975.481 | 0.89748 | 3193.68 | 0.15165 | 1419.31 | 0.68307 | 920.513 | 9.4768 | 1214.3 | 3.0157 | 3561.47 | 0.44036 | 1786.35 | 12.6397 | 2069.22 | 7.3584 | 4276.66 | 1.4075
64.1314 | 0.32137 | 160.763 | 0.22646 | 151.856 | 0.27716 | 219.847 | 0.22897 | 296.169 | 0.20146 | 251.371 | 0.26154 | 416.935 | 0.19453 | 390.697 | 0.26128 | 512.823 | 0.20718 | 533.752 | 0.25483 | 991.214 | 0.14411 | 729.188 | 0.31344 | 886.19 | 0.31977 | 1065.21 | 0.33751 | 1224.06 | 0.41638 | 888.852 | 1.094 | 3022.77 | 0.16395 | 1352.79 | 0.75566 | 893.307 | 12.5892 | 1170.2 | 3.4933 | 3203.27 | 0.5449 | 1738.76 | 18.0085 | 1998.05 | 10.0326 | 4015.54 | 1.7226
59.26 | 0.3365 | 147.515 | 0.24119 | 139.342 | 0.30024 | 201.528 | 0.24804 | 268.253 | 0.22132 | 230.426 | 0.28847 | 384.495 | 0.21221 | 354.579 | 0.29577 | 473.395 | 0.22851 | 485.38 | 0.29021 | 902.285 | 0.16087 | 680.57 | 0.34883 | 795.468 | 0.37978 | 1005.18 | 0.37375 | 1141.3 | 0.469 | 818.056 | 1.319 | 2843.89 | 0.17904 | 1295.86 | 0.8343 | 869.511 | 17.9546 | 1118.7 | 4.3922 | 2971.82 | 0.63753 | 1685.69 | 26.5186 | 1921.63 | 14.2655 | 3823.53 | 2.1167
53.6206 | 0.35766 | 130.442 | 0.26523 | 123.462 | 0.33886 | 186.034 | 0.26789 | 245.656 | 0.24168 | 211.438 | 0.32009 | 352.811 | 0.23336 | 333.596 | 0.32169 | 436.999 | 0.25305 | 442.275 | 0.33149 | 840.444 | 0.17549 | 641.578 | 0.38398 | 727.731 | 0.43816 | 952.348 | 0.41265 | 1053.56 | 0.53732 | 757.43 | 1.5886 | 2689.01 | 0.19375 | 1230.19 | 0.93973 | 842.97 | 26.4656 | 1072.69 | 5.6964 | 2804.35 | 0.72749 | 1630.97 | 38.9721 | 1870.44 | 18.4275 | 3688.33 | 2.5341
48.8588 | 0.37902 | 115.923 | 0.29166 | 108.628 | 0.38823 | 171.903 | 0.28963 | 226.089 | 0.26285 | 195.572 | 0.35199 | 324.061 | 0.25765 | 310.732 | 0.35411 | 404.613 | 0.27994 | 389.916 | 0.40045 | 788.341 | 0.1903 | 597.008 | 0.43207 | 686.037 | 0.48425 | 880.888 | 0.47466 | 984.3 | 0.60825 | 701.297 | 1.9248 | 2509.72 | 0.21477 | 1171.37 | 1.0595 | 815.606 | 38.9332 | 1034.76 | 7.4771 | 2643.68 | 0.83097 | 1579.6 | 55.4149 | 1815.16 | 26.6249 | 3554.35 | 3.1357
45.2378 | 0.39806 | 103.33 | 0.32201 | 97.8987 | 0.43598 | 156.794 | 0.31977 | 207.044 | 0.28905 | 173.284 | 0.41059 | 297.356 | 0.28617 | 286.269 | 0.39647 | 374.627 | 0.31063 | 362.829 | 0.44926 | 725.551 | 0.21264 | 561.679 | 0.47513 | 649.973 | 0.52668 | 832.082 | 0.52721 | 915.922 | 0.69756 | 640.296 | 2.4839 | 2356.49 | 0.23689 | 1116.47 | 1.1899 | 789.919 | 55.3042 | 999.176 | 10.1537 | 2527.35 | 0.93131 | 1526.8 | 82.2571 | 1781 | 35.5467 | 3442.41 | 3.8723
41.5931 | 0.42098 | 92.6597 | 0.35481 | 88.1406 | 0.49403 | 145.755 | 0.3464 | 188.657 | 0.32233 | 153.382 | 0.48522 | 273.672 | 0.31722 | 261.892 | 0.45151 | 351.051 | 0.34056 | 337.286 | 0.503 | 667.094 | 0.23831 | 531.09 | 0.52144 | 616.422 | 0.57859 | 784.409 | 0.59146 | 872.123 | 0.76479 | 592.844 | 3.1545 | 2201.57 | 0.26311 | 1070.55 | 1.3282 | 763.514 | 82.2571 | 960.958 | 14.3801 | 2401.69 | 1.0585 | 1468.4 | 126.576 | 1749.22 | 49.247 | 3354.06 | 4.7107
37.635 | 0.45106 | 83.6745 | 0.39056 | 78.9594 | 0.56657 | 134.684 | 0.3794 | 168.162 | 0.36966 | 140.321 | 0.54982 | 245.901 | 0.36525 | 241.515 | 0.5106 | 323.737 | 0.38245 | 320.516 | 0.54763 | 577.629 | 0.29195 | 509.246 | 0.56093 | 587.532 | 0.63055 | 740.208 | 0.66222 | 832.082 | 0.83681 | 548.908 | 4.3879 | 2065.09 | 0.2905 | 1025.49 | 1.4976 | 734.31 | 126.576 | 935.359 | 18.5755 | 2257.31 | 1.2521 | 1412.23 | 192.26 | 1719.74 | 66.2774 | 3277.8 | 5.829
34.7067 | 0.47751 | 72.2357 | 0.45332 | 70.1008 | 0.66222 | 123.956 | 0.41763 | 150.194 | 0.42649 | 127.222 | 0.63625 | 217.877 | 0.42992 | 212.498 | 0.61992 | 303.06 | 0.42183 | 305.494 | 0.59264 | 504.179 | 0.35802 | 489.768 | 0.60281 | 551.66 | 0.70669 | 701.998 | 0.7348 | 793.879 | 0.92205 | 516.426 | 6.1095 | 1948.72 | 0.31945 | 981.352 | 1.714 | 706.223 | 192.26 | 907.715 | 26.7316 | 2138.65 | 1.4738 | 1370.49 | 281.984 | 1687.37 | 90.3643 | 3216.11 | 6.9022
31.8149 | 0.50907 | 61.9876 | 0.53678 | 62.9874 | 0.76555 | 115.576 | 0.45468 | 138.786 | 0.47229 | 119.933 | 0.69339 | 197.933 | 0.49403 | 192.276 | 0.72749 | 274.22 | 0.49107 | 294.103 | 0.63308 | 457.113 | 0.4168 | 470.564 | 0.64458 | 521.094 | 0.78808 | 669.768 | 0.80803 | 765.042 | 0.99485 | 492.223 | 8.38 | 1846.28 | 0.34814 | 941.93 | 1.9539 | 685.351 | 281.702 | 890.632 | 35.6891 | 2008.07 | 1.7929 | 1333.99 | 386.778 | 1660.59 | 119.923 | 3130.44 | 8.6871
28.8449 | 0.54817 | 55.2536 | 0.61375 | 55.5306 | 0.91836 | 106.797 | 0.502 | 130.182 | 0.51419 | 112.948 | 0.7534 | 175.727 | 0.59028 | 175.551 | 0.84269 | 253.644 | 0.55535 | 278.086 | 0.69617 | 409.498 | 0.4985 | 440.509 | 0.72676 | 490.258 | 0.88678 | 626.364 | 0.92759 | 735.044 | 1.0853 | 476.244 | 11.0545 | 1759.75 | 0.37826 | 905.902 | 2.2498 | 667.094 | 386.392 | 874.744 | 49.3456 | 1912.04 | 2.1899 | 1301.05 | 505.654 | 1632.6 | 162.853 | 3068.45 | 10.5893
26.8948 | 0.58033 | 50.2462 | 0.68993 | 50.1458 | 1.0691 | 98.7838 | 0.5559 | 123.215 | 0.55258 | 106.69 | 0.82353 | 157.108 | 0.70387 | 161.569 | 0.96449 | 231.119 | 0.64329 | 267.182 | 0.7474 | 381.813 | 0.56037 | 417.77 | 0.80641 | 461.246 | 0.99984 | 597.606 | 1.0252 | 706.93 | 1.1863 | 464.486 | 14.0672 | 1677.28 | 0.41265 | 874.744 | 2.5879 | 650.623 | 505.654 | 859.999 | 66.4101 | 1844.43 | 2.6113 | 1282.96 | 599.954 | 1608.29 | 213.119 | 3001.68 | 12.9597
24.6046 | 0.6249 | 46.2904 | 0.76555 | 45.2378 | 1.2484 | 90.6435 | 0.62428 | 116.971 | 0.59502 | 98.3895 | 0.93598 | 143.299 | 0.81289 | 150.796 | 1.0864 | 211.438 | 0.74144 | 257.735 | 0.79759 | 361.38 | 0.61191 | 389.526 | 0.92482 | 439.19 | 1.1039 | 561.679 | 1.1768 | 677.853 | 1.3058 | 454.833 | 18.0807 | 1585.93 | 0.4565 | 848.891 | 2.9531 | 641.578 | 599.954 | 843.813 | 90.5452 | 1777.44 | 3.2118 | 1282.96 | 599.954 | 1590.7 | 261.347 | 2930.5 | 15.9561
22.6222 | 0.67357 | 43.2905 | 0.83681 | 42.0111 | 1.4075 | 83.5073 | 0.70036 | 111.044 | 0.642 | 92.7524 | 1.0324 | 129.144 | 0.96738 | 140.883 | 1.2298 | 188.657 | 0.89928 | 246.887 | 0.86229 | 343.756 | 0.6662 | 367.576 | 1.0375 | 424.084 | 1.191 | 530.559 | 1.3376 | 657.162 | 1.4047 | 443.604 | 24.7505 | 1486.13 | 0.51522 | 818.056 | 3.5003 | 641.578 | 599.954 | 830.419 | 120.043 | 1721.46 | 3.9505 | 1282.96 | 599.954 | 1567.01 | 337.597 | 2872.47 | 19.2372
20.4081 | 0.73996 | 40.8511 | 0.90469 | 39.4855 | 1.5556 | 78.5656 | 0.76555 | 104.682 | 0.69896 | 85.9644 | 1.1698 | 120.173 | 1.094 | 131.358 | 1.3935 | 173.457 | 1.0479 | 234.611 | 0.94823 | 330.277 | 0.71594 | 347.558 | 1.1616 | 407.863 | 1.3006 | 504.179 | 1.5051 | 633.292 | 1.5416 | 434.385 | 32.8794 | 1408 | 0.57112 | 791.501 | 4.1035 | 641.578 | 599.954 | 816.422 | 163.016 | 1677.28 | 4.7915 | 1282.96 | 599.954 | 1543.68 | 431.321 | 2798.75 | 24.4797
18.8203 | 0.80159 | 38.5492 | 0.97808 | 37.3351 | 1.7157 | 74.8087 | 0.82517 | 99.5772 | 0.75265 | 82.0176 | 1.2723 | 112.835 | 1.2224 | 123.092 | 1.5728 | 163.847 | 1.1628 | 221.391 | 1.0617 | 314.169 | 0.78415 | 327.318 | 1.3137 | 395.018 | 1.3907 | 485.865 | 1.6402 | 615.19 | 1.6484 | 428.775 | 44.6051 | 1342.01 | 0.62929 | 764.277 | 5.0221 | 641.578 | 599.954 | 804.267 | 213.119 | 1639.14 | 5.9112 | 1282.96 | 599.954 | 1528.32 | 513.81 | 2746.08 | 29.2198
17.6712 | 0.85628 | 35.8712 | 1.0853 | 35.979 | 1.831 | 69.7511 | 0.91653 | 93.7783 | 0.82517 | 77.5508 | 1.4033 | 106.264 | 1.3564 | 116.855 | 1.7417 | 153.843 | 1.3124 | 208.29 | 1.1982 | 297.952 | 0.86143 | 310.111 | 1.4782 | 382.195 | 1.4946 | 472.45 | 1.7592 | 595.22 | 1.8019 | 421.969 | 63.2344 | 1260.08 | 0.71451 | 739.468 | 6.1278 | 641.578 | 599.954 | 795.468 | 261.347 | 1608.29 | 6.9786 | 1282.96 | 599.954 | 1519.18 | 558.834 | 2680.95 | 36.1923
16.6421 | 0.9147 | 33.4795 | 1.1982 | 34.4991 | 1.9755 | 65.8207 | 1.0038 | 86.309 | 0.94067 | 73.3274 | 1.554 | 101.588 | 1.4797 | 109.939 | 1.9815 | 145.319 | 1.4708 | 198.528 | 1.3203 | 283.988 | 0.94161 | 296.466 | 1.6288 | 367.209 | 1.6435 | 456.2 | 1.9325 | 572.453 | 2.0034 | 417.77 | 82.0107 | 1213.09 | 0.77557 | 715.464 | 7.5371 | 641.578 | 599.954 | 783.625 | 337.597 | 1565.45 | 8.7744 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2625.24 | 44.2496
15.6729 | 0.98299 | 31.6562 | 1.3032 | 33.246 | 2.1145 | 62.423 | 1.0896 | 79.9126 | 1.0638 | 70.2411 | 1.6902 | 96.5377 | 1.6304 | 104.682 | 2.1899 | 136.993 | 1.6617 | 190.363 | 1.4388 | 268.79 | 1.0459 | 282.289 | 1.8346 | 354.579 | 1.7911 | 439.629 | 2.1251 | 554.425 | 2.1833 | 414.441 | 110.592 | 1162.03 | 0.85542 | 695.709 | 9.345 | 641.578 | 599.954 | 771.959 | 431.752 | 1534.45 | 10.6743 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2552.75 | 57.8497
14.8045 | 1.0553 | 29.664 | 1.4388 | 31.9744 | 2.2861 | 58.7878 | 1.2066 | 74.5846 | 1.1934 | 66.7486 | 1.8679 | 92.9381 | 1.7521 | 98.9816 | 2.4765 | 130.703 | 1.8346 | 183.081 | 1.5728 | 256.706 | 1.1409 | 270.678 | 2.0235 | 342.041 | 1.9539 | 421.126 | 2.3818 | 539.116 | 2.3699 | 411.55 | 141.436 | 1106.47 | 0.95872 | 681.251 | 11.3231 | 641.578 | 599.954 | 764.277 | 513.81 | 1501.06 | 13.0507 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2494.71 | 71.7257
14.2098 | 1.1161 | 27.2467 | 1.6402 | 30.8746 | 2.4445 | 56.1448 | 1.3084 | 69.8908 | 1.3349 | 63.3664 | 2.0789 | 89.1155 | 1.9133 | 93.3106 | 2.8203 | 124.453 | 2.0418 | 176.255 | 1.7106 | 244.675 | 1.2546 | 263.204 | 2.1768 | 330.607 | 2.1273 | 407.048 | 2.6191 | 526.331 | 2.5596 | 409.088 | 177.478 | 1064.14 | 1.0532 | 664.431 | 14.237 | 641.578 | 599.954 | 759.706 | 559.393 | 1465.46 | 16.0522 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2435.55 | 90.1838
13.5033 | 1.2018 | 25.4047 | 1.8346 | 29.7234 | 2.6375 | 53.7817 | 1.4132 | 65.5579 | 1.4931 | 60.4571 | 2.2952 | 85.5357 | 2.081 | 89.8313 | 3.0859 | 118.739 | 2.2861 | 170.875 | 1.842 | 232.742 | 1.3894 | 254.66 | 2.3699 | 318.28 | 2.351 | 393.835 | 2.8801 | 515.394 | 2.7342 | 405.018 | 231.794 | 1022.42 | 1.164 | 642.863 | 19.7044 | 641.578 | 599.954 | 757.43 | 599.954 | 1436.45 | 19.3336 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2373.04 | 116.146
12.7934 | 1.3058 | 23.9013 | 2.0235 | 28.7873 | 2.8259 | 51.6729 | 1.5172 | 62.1738 | 1.6452 | 57.7391 | 2.5443 | 81.2827 | 2.3253 | 85.1091 | 3.5143 | 113.061 | 2.575 | 165.163 | 1.9974 | 223.616 | 1.5202 | 246.887 | 2.5983 | 304.884 | 2.6402 | 379.909 | 3.1894 | 504.683 | 2.9798 | 402.595 | 300.922 | 984.3 | 1.2864 | 625.112 | 26.5717 | 641.578 | 599.954 | 757.43 | 599.954 | 1399.58 | 24.5778 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2321.41 | 142.572
11.9763 | 1.4548 | 22.6902 | 2.2052 | 27.6862 | 3.0613 | 49.6965 | 1.6321 | 58.8466 | 1.8255 | 55.1984 | 2.8259 | 77.4733 | 2.5931 | 80.7158 | 4.0384 | 108.086 | 2.8658 | 160.442 | 2.1337 | 212.71 | 1.697 | 239.83 | 2.8175 | 295.873 | 2.8946 | 368.681 | 3.5038 | 494.69 | 3.2376 | 400.187 | 377.606 | 950.445 | 1.4203 | 610.899 | 34.7384 | 641.578 | 599.954 | 757.43 | 599.954 | 1373.24 | 29.3369 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2259.57 | 179.981
11.4036 | 1.5934 | 21.6268 | 2.3961 | 26.5475 | 3.3597 | 47.6048 | 1.768 | 55.8089 | 2.0195 | 52.7695 | 3.1482 | 73.8425 | 2.8859 | 76.3199 | 4.6966 | 103.641 | 3.2054 | 155.233 | 2.3299 | 204.574 | 1.8549 | 231.581 | 3.1076 | 284.272 | 3.2539 | 359.578 | 3.8184 | 484.894 | 3.5038 | 398.589 | 479.073 | 912.265 | 1.5981 | 595.816 | 47.4581 | 641.578 | 599.954 | 757.43 | 599.954 | 1340.67 | 36.2648 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2208.19 | 227.204
10.9128 | 1.7417 | 20.7788 | 2.5801 | 25.532 | 3.6504 | 45.1023 | 1.9481 | 53.1402 | 2.2252 | 50.8527 | 3.4759 | 71.018 | 3.1735 | 73.6213 | 5.2218 | 99.7766 | 3.5674 | 150.345 | 2.529 | 196.749 | 2.0337 | 224.512 | 3.407 | 277.531 | 3.5603 | 349.999 | 4.2074 | 473.869 | 3.853 | 397.793 | 577.584 | 875.619 | 1.8146 | 583.434 | 63.2977 | 641.578 | 599.954 | 757.43 | 599.954 | 1312.81 | 44.3382 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2157.98 | 279.737
10.4744 | 1.9114 | 19.8844 | 2.8006 | 24.6292 | 3.9743 | 43.2905 | 2.1209 | 50.4475 | 2.4641 | 48.6637 | 3.9229 | 68.3016 | 3.5038 | 71.018 | 5.8232 | 96.1523 | 3.9743 | 144.739 | 2.7922 | 189.792 | 2.2274 | 216.357 | 3.7767 | 268.522 | 3.9783 | 343.412 | 4.5442 | 464.486 | 4.2242 | 397.793 | 599.954 | 837.927 | 2.0872 | 571.881 | 88.3096 | 641.578 | 599.954 | 757.43 | 599.954 | 1276.56 | 57.9655 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2113.14 | 339.628
10.1141 | 2.0747 | 19.1429 | 3.0187 | 23.8536 | 4.301 | 41.2204 | 2.3323 | 47.9392 | 2.7452 | 46.99 | 4.366 | 65.1657 | 3.9663 | 68.5069 | 6.559 | 93.2173 | 4.4099 | 139.621 | 3.1076 | 181.623 | 2.4964 | 209.543 | 4.1906 | 263.995 | 4.3312 | 336.276 | 4.9622 | 456.656 | 4.5807 | 397.793 | 599.954 | 813.976 | 2.3323 | 561.679 | 120.283 | 641.578 | 599.954 | 757.43 | 599.954 | 1247.54 | 71.8693 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2065.09 | 424.899
9.8054 | 2.2498 | 18.3739 | 3.2833 | 23.1717 | 4.6174 | 39.3279 | 2.5673 | 45.3284 | 3.1045 | 45.3738 | 4.8834 | 62.9244 | 4.3442 | 66.3493 | 7.3584 | 90.5529 | 4.9079 | 134.28 | 3.4828 | 173.457 | 2.8203 | 204.984 | 4.5396 | 257.735 | 4.7915 | 329.287 | 5.4403 | 449.858 | 4.9276 | 397.793 | 599.954 | 787.553 | 2.6349 | 553.871 | 161.233 | 641.578 | 599.954 | 757.43 | 599.954 | 1217.95 | 90.274 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2020.15 | 519.493
9.4021 | 2.5215 | 17.742 | 3.5461 | 22.0858 | 5.2375 | 37.7858 | 2.7894 | 43.5511 | 3.4241 | 43.7694 | 5.484 | 60.9427 | 4.7676 | 64.5173 | 8.2223 | 88.1406 | 5.4786 | 128.757 | 3.9584 | 166.157 | 3.1672 | 199.923 | 4.9622 | 252.884 | 5.2585 | 322.122 | 6.0306 | 442.275 | 5.3647 | 397.793 | 599.954 | 765.042 | 2.959 | 546.717 | 227.887 | 641.578 | 599.954 | 757.43 | 599.954 | 1186.69 | 116.262 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1986.1 | 596.962
9.1334 | 2.7452 | 17.166 | 3.807 | 21.3902 | 5.7307 | 35.9071 | 3.1107 | 41.8016 | 3.7616 | 42.1373 | 6.2205 | 58.7878 | 5.3167 | 62.8615 | 9.1783 | 85.4502 | 6.2329 | 125.202 | 4.3747 | 160.121 | 3.5496 | 195.572 | 5.4132 | 248.373 | 5.8465 | 316.692 | 6.5919 | 435.69 | 5.8232 | 397.793 | 599.954 | 744.662 | 3.3362 | 540.736 | 310.707 | 641.578 | 599.954 | 757.43 | 599.954 | 1160.87 | 142.715 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
8.8901 | 3.0187 | 16.5425 | 4.1406 | 20.7788 | 6.2392 | 34.6374 | 3.3597 | 40.1224 | 4.1614 | 40.7695 | 7.0065 | 57.2217 | 5.8115 | 60.9427 | 10.5049 | 83.3404 | 7.0417 | 122.355 | 4.7724 | 154.768 | 3.9465 | 191.126 | 6.0125 | 243.211 | 6.5919 | 311.043 | 7.2489 | 429.203 | 6.3971 | 397.793 | 599.954 | 725.551 | 3.7729 | 536.427 | 403.773 | 641.578 | 599.954 | 757.43 | 599.954 | 1129.95 | 179.981 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
8.7141 | 3.2767 | 15.9098 | 4.5396 | 20.2455 | 6.7318 | 33.513 | 3.6177 | 38.5106 | 4.6082 | 39.525 | 7.8841 | 55.6418 | 6.4163 | 59.557 | 11.9633 | 80.7965 | 8.38 | 119.693 | 5.306 | 150.495 | 4.2924 | 187.341 | 6.5985 | 237.206 | 7.5522 | 304.884 | 8.0032 | 420.705 | 7.1624 | 397.793 | 599.954 | 704.107 | 4.3922 | 533.752 | 503.132 | 641.578 | 599.954 | 757.43 | 599.954 | 1104.26 | 227.204 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
8.5074 | 3.6504 | 15.3319 | 4.9771 | 19.7062 | 7.3584 | 32.5551 | 3.8607 | 37.0376 | 5.1082 | 38.5106 | 8.8184 | 54.1595 | 7.0206 | 58.6703 | 13.4482 | 78.6442 | 9.9031 | 117.206 | 5.9349 | 147.515 | 4.6221 | 183.448 | 7.3437 | 232.742 | 8.5151 | 297.952 | 9.1875 | 411.55 | 8.116 | 397.793 | 599.954 | 686.037 | 5.0573 | 532.153 | 556.047 | 641.578 | 599.954 | 757.43 | 599.954 | 1079.15 | 279.737 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
8.3223 | 4.0586 | 14.9085 | 5.354 | 19.2774 | 7.9315 | 31.4668 | 4.178 | 35.9071 | 5.5503 | 37.5222 | 9.8833 | 52.8223 | 7.7125 | 57.5661 | 15.5466 | 76.5492 | 11.9513 | 114.312 | 6.7385 | 144.739 | 4.9622 | 179.995 | 8.1404 | 228.362 | 9.6489 | 292.344 | 10.2969 | 403.805 | 9.16 | 397.793 | 599.954 | 668.43 | 5.8876 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 1056.72 | 339.968 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
8.1331 | 4.6267 | 14.4535 | 5.8582 | 18.8203 | 8.6785 | 30.3845 | 4.5669 | 35.0556 | 5.9112 | 36.6691 | 10.9555 | 51.6213 | 8.4896 | 56.5392 | 18.3907 | 74.6592 | 14.4233 | 112.61 | 7.5146 | 142.299 | 5.3701 | 176.431 | 9.1143 | 224.064 | 11.1545 | 286.842 | 11.703 | 398.589 | 10.1031 | 397.793 | 599.954 | 649.973 | 7.0487 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 1032.69 | 425.324 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
8.012 | 5.1389 | 14.0403 | 6.4099 | 18.3923 | 9.4768 | 29.3982 | 4.9671 | 34.19 | 6.3588 | 36.051 | 12.1441 | 50.7004 | 9.2891 | 55.6418 | 22.3504 | 72.9616 | 17.9905 | 110.049 | 8.7394 | 139.9 | 5.8232 | 173.978 | 10.1334 | 219.847 | 12.895 | 281.443 | 13.5021 | 393.835 | 11.2216 | 397.793 | 599.954 | 636.466 | 8.0756 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 1010.22 | 519.493 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.869 | 5.7941 | 13.6526 | 7.077 | 18.0823 | 10.2969 | 28.4439 | 5.4567 | 33.4126 | 6.8472 | 35.5143 | 13.3945 | 49.8458 | 10.2148 | 54.978 | 26.8119 | 72.0193 | 20.2235 | 107.978 | 10.0527 | 137.542 | 6.3779 | 170.704 | 11.3571 | 215.494 | 15.2998 | 276.699 | 15.4382 | 387.583 | 12.6903 | 397.793 | 599.954 | 621.994 | 9.572 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 993.199 | 596.962 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.7596 | 6.5722 | 13.4091 | 7.5901 | 17.7597 | 11.188 | 27.274 | 6.0973 | 32.751 | 7.3217 | 35.0205 | 15.3612 | 49.202 | 11.1211 | 54.5945 | 32.4872 | 71.374 | 22.7791 | 105.84 | 11.6213 | 135.088 | 7.1053 | 167.994 | 12.7158 | 210.804 | 18.3173 | 272.307 | 17.5112 | 381.813 | 14.4521 | 397.793 | 599.954 | 609.678 | 11.2891 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.6441 | 7.4472 | 13.078 | 8.3632 | 17.4953 | 12.1198 | 26.5475 | 6.5985 | 31.9744 | 7.9394 | 34.4991 | 18.2807 | 48.276 | 12.6271 | 54.5945 | 40.0387 | 70.4522 | 26.7583 | 103.952 | 13.6105 | 132.546 | 7.9236 | 165.825 | 14.1518 | 206.424 | 22.9162 | 267.985 | 20.1427 | 376.505 | 16.1973 | 397.793 | 599.954 | 596.412 | 13.4751 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.5378 | 8.3465 | 12.7296 | 9.252 | 17.2866 | 13.2877 | 25.8144 | 7.1552 | 31.404 | 8.5236 | 34.1559 | 20.7562 | 47.32 | 14.612 | 54.5945 | 49.3456 | 69.8209 | 30.6872 | 101.996 | 16.4585 | 130.573 | 8.792 | 163.519 | 15.6245 | 202.741 | 28.6412 | 262.416 | 24.309 | 371.642 | 18.4091 | 397.793 | 599.954 | 584.018 | 16.475 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.4479 | 9.4863 | 12.4526 | 10.266 | 17.0634 | 14.6852 | 25.1771 | 7.7048 | 30.7821 | 9.1692 | 33.816 | 24.701 | 46.6155 | 16.8583 | 54.5945 | 65.356 | 69.1954 | 35.5822 | 99.4777 | 21.4311 | 128.5 | 9.8438 | 161.407 | 17.6166 | 199.125 | 35.0174 | 258.768 | 27.8782 | 366.842 | 21.1543 | 397.793 | 599.954 | 574.748 | 19.103 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.3738 | 10.9555 | 12.1939 | 11.4827 | 16.8767 | 16.2135 | 24.7032 | 8.28 | 30.2028 | 10.0627 | 33.6137 | 28.958 | 45.8756 | 19.9822 | 54.5945 | 85.6997 | 68.5069 | 43.7218 | 98.0947 | 25.7091 | 126.587 | 11.0324 | 159.482 | 19.8627 | 195.768 | 46.0555 | 255.17 | 32.2283 | 360.298 | 24.6763 | 397.793 | 599.954 | 565.625 | 22.8247 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.3078 | 12.9986 | 11.9644 | 13.2347 | 16.6921 | 18.0988 | 24.2383 | 8.8626 | 29.7531 | 10.7601 | 33.5466 | 34.0846 | 45.4646 | 23.6377 | 54.5945 | 123.822 | 67.8931 | 54.4808 | 97.0216 | 30.2303 | 124.952 | 12.2294 | 157.58 | 22.5074 | 192.661 | 59.3735 | 251.623 | 37.1828 | 354.934 | 28.3846 | 397.793 | 599.954 | 555.535 | 27.3535 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.2423 | 15.4536 | 11.8335 | 14.5391 | 16.5425 | 20.2842 | 23.8536 | 9.5816 | 29.2809 | 11.8088 | 33.4795 | 39.6007 | 45.0122 | 27.7392 | 54.5945 | 170.179 | 67.3521 | 67.9552 | 95.7685 | 36.9974 | 123.215 | 14.1235 | 155.856 | 26.1238 | 189.792 | 75.7054 | 248.125 | 42.9848 | 350.349 | 33.4431 | 397.793 | 599.954 | 547.811 | 31.9715 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.1918 | 18.3173 | 11.6923 | 16.2135 | 16.3943 | 22.7791 | 23.4749 | 10.39 | 28.9895 | 12.665 | 33.3125 | 47.4581 | 44.6089 | 33.1435 | 54.5945 | 228.343 | 66.8823 | 88.575 | 95.0054 | 43.2435 | 121.38 | 16.1973 | 154.151 | 29.3662 | 187.341 | 95.0924 | 245.165 | 48.5623 | 345.133 | 39.3638 | 397.793 | 599.954 | 538.039 | 38.3152 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.1416 | 22.0397 | 11.5992 | 18.1169 | 16.2637 | 25.7606 | 23.0792 | 11.3571 | 28.7298 | 13.6924 | 33.1796 | 57.3887 | 44.3864 | 39.3245 | 54.5945 | 306.388 | 66.3493 | 117.43 | 93.8721 | 52.9765 | 119.933 | 18.9129 | 152.312 | 34.4616 | 184.737 | 124.443 | 242.24 | 56.4214 | 340.335 | 47.08 | 397.793 | 599.954 | 530.559 | 45.9175 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.1416 | 25.6065 | 11.5182 | 20.4063 | 16.1502 | 29.1906 | 22.804 | 12.2539 | 28.3587 | 15.5933 | 33.0802 | 69.4668 | 44.1651 | 49.6425 | 54.54 | 429.599 | 66.1506 | 161.555 | 93.0311 | 67.4137 | 118.384 | 22.128 | 150.495 | 40.9703 | 182.716 | 159.469 | 239.112 | 64.5764 | 336.612 | 57.5036 | 397.793 | 599.954 | 522.66 | 54.0467 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.1202 | 31.0577 | 11.4608 | 22.7336 | 16.0536 | 32.5848 | 22.5319 | 13.3945 | 28.302 | 17.8293 | 32.9811 | 84.9319 | 44.0768 | 60.4519 | 54.54 | 520.533 | 65.8865 | 210.577 | 92.0134 | 86.1293 | 117.206 | 25.5298 | 148.551 | 53.6697 | 181.26 | 207.027 | 236.023 | 76.7727 | 333.596 | 67.6163 | 397.793 | 599.954 | 514.879 | 64.8352 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.106 | 37.707 | 11.3809 | 26.1499 | 15.9416 | 37.7448 | 22.2854 | 14.5101 | 28.302 | 20.6114 | 32.9152 | 98.4796 | 44.0768 | 77.0034 | 54.54 | 577.584 | 65.8865 | 270.657 | 91.3715 | 105.093 | 116.155 | 29.7803 | 147.368 | 64.2543 | 179.995 | 259.006 | 233.441 | 88.93 | 330.277 | 83.5002 | 397.793 | 599.954 | 506.2 | 85.614 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0989 | 50.8484 | 11.3581 | 30.5953 | 15.8939 | 43.4603 | 22.13 | 15.8924 | 28.302 | 24.5287 | 32.9152 | 120.283 | 44.0328 | 104.047 | 54.54 | 599.954 | 65.8865 | 332.903 | 90.8249 | 126.83 | 114.885 | 36.0118 | 146.193 | 76.6193 | 178.74 | 325.985 | 230.888 | 101.681 | 327.645 | 104.36 | 397.793 | 599.954 | 498.663 | 110.371 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0705 | 64.641 | 11.3468 | 35.2282 | 15.8621 | 49.9413 | 21.9976 | 17.4413 | 28.302 | 29.1614 | 32.9152 | 147.208 | 43.9888 | 131.085 | 54.54 | 599.954 | 65.8865 | 415.238 | 90.3719 | 155.221 | 113.969 | 42.9419 | 144.884 | 98.2829 | 177.493 | 415.654 | 228.133 | 122.223 | 326.011 | 127.849 | 397.793 | 599.954 | 492.223 | 139.33 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0635 | 116.845 | 11.3468 | 119.324 | 15.8621 | 58.0816 | 21.8879 | 19.1221 | 28.302 | 35.3694 | 32.9152 | 184.721 | 43.8132 | 176.947 | 54.54 | 599.954 | 65.8865 | 491.692 | 89.8313 | 201.915 | 113.061 | 52.1356 | 144.017 | 115.567 | 176.431 | 499.123 | 225.864 | 146.914 | 323.737 | 167.813 | 397.793 | 599.954 | 485.38 | 185.276 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 317.301 | 11.3468 | 149.732 | 15.8463 | 69.6059 | 21.8879 | 39.0111 | 28.302 | 45.8258 | 32.9152 | 229.717 | 43.7694 | 239.092 | 54.54 | 599.954 | 65.8865 | 566.713 | 89.3833 | 255.916 | 112.497 | 61.3655 | 142.869 | 141.153 | 175.903 | 559.953 | 223.616 | 178.19 | 323.09 | 205.583 | 397.793 | 599.954 | 480.55 | 232.491 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 485.341 | 11.3354 | 599.954 | 15.8463 | 504.644 | 21.8879 | 94.8076 | 28.302 | 59.3142 | 32.9152 | 272.013 | 43.6819 | 305.775 | 54.54 | 599.954 | 65.8865 | 599.954 | 88.7598 | 336.585 | 111.601 | 75.1021 | 142.299 | 170.861 | 175.2 | 599.954 | 221.391 | 209.108 | 322.767 | 271.741 | 397.793 | 599.954 | 475.768 | 301.223 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 544.492 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 156.467 | 28.302 | 75.0271 | 32.9152 | 367.547 | 43.6382 | 375.723 | 54.54 | 599.954 | 65.8865 | 599.954 | 88.3171 | 422.78 | 111.267 | 87.169 | 141.873 | 216.556 | 175.2 | 599.954 | 220.067 | 251.854 | 322.445 | 342.014 | 397.793 | 599.954 | 471.506 | 379.499 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 347.183 | 28.302 | 87.169 | 32.9152 | 453.889 | 43.464 | 474.306 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.8766 | 513.81 | 110.712 | 106.149 | 141.731 | 278.621 | 175.2 | 599.954 | 218.75 | 299.421 | 322.122 | 418.992 | 397.793 | 599.954 | 468.217 | 486.8 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 108.51 | 32.9152 | 529.987 | 43.3772 | 551.065 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.701 | 578.74 | 110.27 | 127.721 | 141.306 | 359.909 | 175.2 | 599.954 | 217.659 | 362.437 | 322.122 | 528.928 | 397.793 | 599.954 | 465.881 | 570.694 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 130.171 | 32.9152 | 573.555 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 109.939 | 174.138 | 141.306 | 461.21 | 175.2 | 599.954 | 216.357 | 446.684 | 321.479 | 578.161 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 164.984 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 109.61 | 223.822 | 141.306 | 570.124 | 175.2 | 599.954 | 215.494 | 553.827 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 205.994 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 109.391 | 282.549 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 248.85 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 108.954 | 348.226 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 302.43 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 108.519 | 424.899 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 377.984 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 108.194 | 488.751 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 467.712 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 107.87 | 569.554 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 553.274 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 107.762 | 599.954 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 599.954 | 28.302 | 599.954 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 107.762 | 599.954 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954