## 165_62U
S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links
Universal and Extra Performance Styles | [9 empty] | Universal and Extra Performance Styles | [9 empty] | Universal and Extra Performance Styles
"K" Speed (TCC 165-6-2) | [9 empty] | "K" Speed (TCC 165-6-2) | [9 empty] | "K" Speed (TCC 165-6-2)
Total Clearing Time-Current Characteristic Curves Dated January 20, 1986 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated January 20, 1986 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated January 20, 1986
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
6K |  | 8K |  | 10K |  | 12K |  | 15K |  | 20K |  | 25K |  | 30K |  | 40K |  | 50K |  | 65K |  | 80K |  | 100K |  | 140K |  | 200K
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
10000 | 0.013298 | 10000 | 0.013298 | 10000 | 0.013298 | 10000 | 0.013298 | 10000 | 0.013298 | 10000 | 0.013298 | 10000 | 0.013404 | 10000 | 0.013499 | 10000 | 0.013826 | 10000 | 0.014134 | 10000 | 0.014564 | 10000 | 0.015357 | 10000 | 0.016145 | 10000 | 0.022144 | 10000 | 0.035149
2766.51 | 0.013485 | 2763.74 | 0.013485 | 2802.7 | 0.013472 | 3798.42 | 0.013593 | 3925.86 | 0.013621 | 5117.09 | 0.013539 | 6256.27 | 0.013607 | 8336.01 | 0.013621 | 8658.87 | 0.013938 | 8789.74 | 0.014205 | 9030.29 | 0.014711 | 9185.12 | 0.015543 | 9408.23 | 0.01652 | 9617.5 | 0.02291 | 9398.82 | 0.037848
2393.09 | 0.013512 | 2385.92 | 0.013512 | 2393.09 | 0.013566 | 3191.8 | 0.013634 | 3502.88 | 0.013771 | 4488.8 | 0.013716 | 5390.21 | 0.013785 | 7363.86 | 0.01373 | 7641.43 | 0.014064 | 7913.62 | 0.014348 | 8105.84 | 0.014933 | 8419.79 | 0.015904 | 8693.58 | 0.017109 | 8994.24 | 0.024351 | 8780.95 | 0.041289
2156.71 | 0.013539 | 2086.7 | 0.013566 | 2167.52 | 0.013689 | 2902.54 | 0.013662 | 3141.14 | 0.013938 | 4001.16 | 0.013896 | 4752.09 | 0.013965 | 6524.63 | 0.013896 | 6969.79 | 0.014205 | 7153.38 | 0.014579 | 7527.66 | 0.015144 | 7772.44 | 0.016356 | 8113.95 | 0.017718 | 8512.92 | 0.025728 | 8162.78 | 0.045449
1961.26 | 0.013566 | 1803.24 | 0.013662 | 1959.29 | 0.013813 | 2615.84 | 0.013771 | 2879.41 | 0.014064 | 3653.13 | 0.014078 | 4369.22 | 0.014148 | 5833.31 | 0.014106 | 6325.47 | 0.014376 | 6492.09 | 0.014785 | 6818.13 | 0.015496 | 7268.75 | 0.01682 | 7595.72 | 0.018404 | 8113.95 | 0.02702 | 7610.93 | 0.050028
1797.84 | 0.013593 | 1652.99 | 0.013744 | 1783.51 | 0.013951 | 2400.28 | 0.013882 | 2658.03 | 0.014248 | 3335.37 | 0.014276 | 4021.22 | 0.014362 | 5331.25 | 0.014319 | 5792.62 | 0.014608 | 6023 | 0.015008 | 6218.85 | 0.01592 | 6784.12 | 0.017385 | 7131.95 | 0.019155 | 7788.01 | 0.028207 | 7068.05 | 0.05579
1671.27 | 0.013607 | 1524.37 | 0.013854 | 1630.01 | 0.01412 | 2145.96 | 0.014092 | 2429.26 | 0.014477 | 3054.41 | 0.014492 | 3697.23 | 0.014608 | 4843.25 | 0.014579 | 5230.91 | 0.014918 | 5526.67 | 0.015327 | 5740.72 | 0.016405 | 6344.48 | 0.017986 | 6683.12 | 0.020097 | 7393.38 | 0.029743 | 6730.07 | 0.060135
1561.4 | 0.013634 | 1391.78 | 0.013993 | 1486.74 | 0.014348 | 1901.39 | 0.014348 | 2209.1 | 0.01474 | 2728.04 | 0.014844 | 3352.09 | 0.014933 | 4461.95 | 0.014859 | 4752.09 | 0.015204 | 5127.33 | 0.015699 | 5374.07 | 0.016871 | 5903.73 | 0.018776 | 6319.15 | 0.020918 | 6976.76 | 0.031645 | 6344.48 | 0.065996
1451.48 | 0.013689 | 1271.99 | 0.014162 | 1349.3 | 0.014623 | 1718.73 | 0.014637 | 1990.9 | 0.015083 | 2520.82 | 0.015129 | 3030.07 | 0.015311 | 4143.68 | 0.015083 | 4421.97 | 0.015465 | 4733.12 | 0.016177 | 5045.95 | 0.017367 | 5411.82 | 0.019977 | 5939.26 | 0.022012 | 6603.4 | 0.033804 | 6023 | 0.071923
1354.71 | 0.013744 | 1167.17 | 0.014348 | 1236.87 | 0.014888 | 1544.32 | 0.014948 | 1830.49 | 0.015403 | 2322.36 | 0.015434 | 2772.04 | 0.015667 | 3806.02 | 0.015373 | 4065.7 | 0.015841 | 4408.72 | 0.016736 | 4718.94 | 0.017968 | 5076.31 | 0.020918 | 5521.14 | 0.023443 | 6275.07 | 0.035931 | 5655.25 | 0.079885
1253.05 | 0.013826 | 1070.99 | 0.014608 | 1138.35 | 0.015189 | 1415.64 | 0.01525 | 1636.54 | 0.015825 | 2141.67 | 0.015778 | 2548.7 | 0.016096 | 3426.66 | 0.015809 | 3802.22 | 0.016193 | 4114.78 | 0.017385 | 4426.39 | 0.018682 | 4695.41 | 0.022322 | 5230.91 | 0.024571 | 5998.95 | 0.038038 | 5320.59 | 0.088818
1169.51 | 0.013882 | 964.242 | 0.014963 | 1037.26 | 0.015527 | 1309.42 | 0.015527 | 1495.68 | 0.016258 | 2010.9 | 0.01608 | 2334 | 0.016636 | 3128.6 | 0.016258 | 3591.55 | 0.016586 | 3848.12 | 0.018058 | 4135.4 | 0.019582 | 4377.97 | 0.02375 | 4955.93 | 0.025935 | 5740.72 | 0.04035 | 4950.98 | 0.10115
1060.33 | 0.014035 | 869.869 | 0.015311 | 949.887 | 0.015936 | 1212.38 | 0.015888 | 1372.43 | 0.016736 | 1858.16 | 0.016537 | 2156.71 | 0.017194 | 2862.18 | 0.016803 | 3395.95 | 0.017057 | 3613.17 | 0.018814 | 3875.15 | 0.020503 | 4005.17 | 0.025857 | 4667.32 | 0.027456 | 5444.39 | 0.043232 | 4584.06 | 0.11658
971.016 | 0.014191 | 781.6 | 0.015683 | 862.076 | 0.016454 | 1114.7 | 0.016356 | 1277.09 | 0.017177 | 1688.07 | 0.017194 | 2012.92 | 0.017736 | 2658.03 | 0.017333 | 3172.71 | 0.017665 | 3368.9 | 0.019818 | 3631.28 | 0.021576 | 3730.66 | 0.027677 | 4444.13 | 0.028806 | 5127.33 | 0.047068 | 4252.83 | 0.13464
883.016 | 0.014391 | 703.694 | 0.016177 | 797.389 | 0.016905 | 1024.89 | 0.016922 | 1175.37 | 0.017825 | 1578.67 | 0.017665 | 1869.34 | 0.018386 | 2451.22 | 0.017932 | 2955.25 | 0.018386 | 3179.06 | 0.02073 | 3338.71 | 0.023257 | 3399.35 | 0.030496 | 4240.09 | 0.030283 | 4882.15 | 0.05038 | 3949.48 | 0.15596
798.986 | 0.014637 | 645.06 | 0.016686 | 741.995 | 0.017437 | 966.173 | 0.017402 | 1106.92 | 0.018423 | 1488.22 | 0.018148 | 1734.27 | 0.01929 | 2262.76 | 0.01872 | 2741.72 | 0.019309 | 2984.96 | 0.021815 | 3094.37 | 0.024893 | 3116.11 | 0.033636 | 4033.3 | 0.031899 | 4634.76 | 0.05463 | 3656.79 | 0.18211
724.399 | 0.014903 | 591.312 | 0.017315 | 684.948 | 0.018076 | 896.361 | 0.018058 | 1044.55 | 0.019098 | 1391.78 | 0.018814 | 1594.54 | 0.020421 | 2088.79 | 0.01966 | 2574.32 | 0.020198 | 2777.59 | 0.023257 | 2853.61 | 0.026912 | 2847.91 | 0.03721 | 3828.93 | 0.033838 | 4382.35 | 0.059656 | 3447.28 | 0.20718
660.068 | 0.01525 | 548.585 | 0.01786 | 643.128 | 0.018739 | 828.273 | 0.018965 | 971.987 | 0.020077 | 1292.51 | 0.01964 | 1480.8 | 0.021598 | 1945.63 | 0.020668 | 2414.72 | 0.021234 | 2610.61 | 0.024547 | 2592.4 | 0.029654 | 2597.59 | 0.041955 | 3667.77 | 0.035573 | 4118.9 | 0.065667 | 3302.19 | 0.22874
608.711 | 0.015589 | 508.947 | 0.018589 | 599.049 | 0.019562 | 766.123 | 0.020037 | 907.182 | 0.021107 | 1223.34 | 0.02034 | 1393.17 | 0.022728 | 1805.04 | 0.022012 | 2271.83 | 0.022367 | 2451.22 | 0.026039 | 2381.15 | 0.032642 | 2400.28 | 0.046646 | 3468.02 | 0.037886 | 3886.8 | 0.072283 | 3141.14 | 0.25662
557.991 | 0.01608 | 474.539 | 0.019542 | 564.163 | 0.020421 | 713.615 | 0.02117 | 841.632 | 0.022547 | 1153.25 | 0.021107 | 1318.62 | 0.023821 | 1679.65 | 0.02349 | 2133.12 | 0.023679 | 2260.5 | 0.028179 | 2178.39 | 0.036183 | 2198.08 | 0.053069 | 3292.3 | 0.040552 | 3704.64 | 0.078225 | 2984.96 | 0.29195
512.522 | 0.016703 | 434.564 | 0.02098 | 530.247 | 0.021426 | 644.415 | 0.023141 | 777.702 | 0.024157 | 1079.59 | 0.022322 | 1236.87 | 0.025295 | 1536.62 | 0.025498 | 1965.18 | 0.025523 | 2070.07 | 0.030957 | 1961.26 | 0.04133 | 2029.08 | 0.059536 | 3094.37 | 0.043754 | 3461.09 | 0.087934 | 2873.66 | 0.32041
477.872 | 0.017263 | 402.761 | 0.022524 | 493.411 | 0.022887 | 586.6 | 0.025244 | 728.759 | 0.02578 | 1006.6 | 0.023774 | 1148.65 | 0.027129 | 1393.17 | 0.028067 | 1825.01 | 0.027456 | 1922.42 | 0.033568 | 1765.77 | 0.047636 | 1901.39 | 0.06593 | 2879.41 | 0.048356 | 3302.19 | 0.095736 | 2714.44 | 0.373
442.015 | 0.017932 | 372.912 | 0.024278 | 453.204 | 0.024893 | 536.648 | 0.027511 | 658.091 | 0.028548 | 928.289 | 0.02578 | 1062.46 | 0.029388 | 1231.93 | 0.031995 | 1698.23 | 0.029683 | 1787.08 | 0.036583 | 1556.72 | 0.056974 | 1778.17 | 0.073009 | 2690.12 | 0.053388 | 3106.77 | 0.10612 | 2569.18 | 0.43467
411.72 | 0.018682 | 349.794 | 0.026065 | 410.487 | 0.027732 | 481.229 | 0.030802 | 599.648 | 0.031709 | 845.005 | 0.028377 | 982.738 | 0.031868 | 1095.91 | 0.036693 | 1581.83 | 0.032027 | 1662.94 | 0.040108 | 1415.64 | 0.065732 | 1677.97 | 0.079965 | 2470.91 | 0.060315 | 2922.93 | 0.11858 | 2441.43 | 0.503
381.97 | 0.019699 | 323.223 | 0.028377 | 381.97 | 0.030253 | 434.999 | 0.034522 | 539.878 | 0.035966 | 758.5 | 0.031995 | 919.052 | 0.034418 | 986.677 | 0.041955 | 1461.68 | 0.035184 | 1542.78 | 0.044327 | 1289.92 | 0.076065 | 1567.66 | 0.089174 | 2324.69 | 0.066062 | 2741.72 | 0.13356 | 2334 | 0.5757
349.095 | 0.021064 | 296.588 | 0.031237 | 353.309 | 0.033168 | 397.559 | 0.038459 | 482.675 | 0.041537 | 662.714 | 0.037773 | 854.352 | 0.037472 | 888.33 | 0.048211 | 1354.71 | 0.038574 | 1409.99 | 0.050028 | 1155.56 | 0.091615 | 1447.13 | 0.10186 | 2143.81 | 0.074933 | 2569.18 | 0.15211 | 2229.07 | 0.6662
322.255 | 0.022547 | 262.787 | 0.035823 | 324.194 | 0.037099 | 357.217 | 0.044238 | 432.397 | 0.048356 | 573.836 | 0.046044 | 791.827 | 0.041454 | 810.25 | 0.055014 | 1259.33 | 0.042376 | 1288.64 | 0.057088 | 1047.69 | 0.10719 | 1331.87 | 0.1174 | 1984.93 | 0.084995 | 2405.08 | 0.17392 | 2156.71 | 0.73848
299.569 | 0.024109 | 236.357 | 0.040837 | 294.519 | 0.042376 | 326.798 | 0.050128 | 388.131 | 0.056633 | 502.373 | 0.055845 | 744.225 | 0.044952 | 739.033 | 0.063029 | 1142.92 | 0.048453 | 1176.55 | 0.065274 | 971.016 | 0.12268 | 1225.79 | 0.13626 | 1817.72 | 0.097963 | 2235.77 | 0.20166 | 2114.01 | 0.79203
274.059 | 0.026248 | 214.507 | 0.046553 | 268.095 | 0.048501 | 297.182 | 0.057546 | 351.899 | 0.065601 | 427.239 | 0.071421 | 685.633 | 0.050329 | 654.809 | 0.075761 | 1025.91 | 0.056463 | 1083.92 | 0.074261 | 875.98 | 0.14835 | 1134.94 | 0.15705 | 1703.33 | 0.10946 | 2037.22 | 0.24216 | 2070.07 | 0.84353
245.511 | 0.029241 | 193.126 | 0.053979 | 242.825 | 0.056125 | 267.56 | 0.067531 | 318.73 | 0.076753 | 379.306 | 0.086625 | 632.287 | 0.056633 | 575.56 | 0.093465 | 940.435 | 0.064495 | 989.642 | 0.085935 | 777.702 | 0.18504 | 1051.88 | 0.18138 | 1561.4 | 0.12705 | 1858.16 | 0.29283 | 2039.26 | 0.88855
221.261 | 0.03274 | 176.857 | 0.061472 | 213.437 | 0.068415 | 241.856 | 0.07909 | 291.88 | 0.088552 | 335.406 | 0.10708 | 585.428 | 0.063853 | 522.353 | 0.11012 | 850.941 | 0.075384 | 901.755 | 0.10004 | 710.055 | 0.22087 | 971.016 | 0.21179 | 1450.03 | 0.14498 | 1715.29 | 0.34571 | 1984.93 | 0.97223
199.805 | 0.03684 | 160.187 | 0.071635 | 192.933 | 0.080446 | 214.937 | 0.096215 | 266.492 | 0.10268 | 302.579 | 0.12807 | 532.372 | 0.074187 | 474.539 | 0.12988 | 778.48 | 0.087321 | 824.967 | 0.1167 | 639.28 | 0.2714 | 894.57 | 0.24904 | 1334.54 | 0.16861 | 1599.33 | 0.40246 | 1930.12 | 1.067
186.483 | 0.040189 | 144.076 | 0.08474 | 171.287 | 0.098356 | 195.849 | 0.1128 | 243.799 | 0.11989 | 270.79 | 0.15596 | 465.142 | 0.092721 | 432.397 | 0.15379 | 714.329 | 0.10135 | 753.209 | 0.13695 | 573.836 | 0.33482 | 809.44 | 0.30509 | 1241.83 | 0.19337 | 1507.7 | 0.4565 | 1871.21 | 1.1804
173.355 | 0.044327 | 130.757 | 0.099742 | 154.368 | 0.1174 | 174.748 | 0.1375 | 221.704 | 0.14239 | 242.34 | 0.19259 | 420.457 | 0.11045 | 388.131 | 0.1869 | 647.645 | 0.11894 | 678.811 | 0.1661 | 521.831 | 0.40569 | 737.557 | 0.36819 | 1160.19 | 0.22087 | 1428.44 | 0.51368 | 1810.47 | 1.3269
163.423 | 0.048163 | 117.842 | 0.11918 | 139.26 | 0.14112 | 159.388 | 0.16346 | 202.015 | 0.16962 | 215.152 | 0.24095 | 371.795 | 0.13708 | 351.196 | 0.22556 | 597.254 | 0.13695 | 594.276 | 0.21137 | 475.489 | 0.49107 | 674.751 | 0.44612 | 1068.85 | 0.25816 | 1361.5 | 0.57398 | 1741.22 | 1.5324
150.106 | 0.05463 | 105.672 | 0.14527 | 123.76 | 0.17549 | 144.654 | 0.19727 | 183.891 | 0.20287 | 193.126 | 0.29785 | 337.763 | 0.1633 | 318.73 | 0.27032 | 550.234 | 0.15895 | 548.585 | 0.2468 | 445.565 | 0.56374 | 615.443 | 0.54055 | 988.652 | 0.30054 | 1282.21 | 0.66023 | 1672.94 | 1.7751
138.704 | 0.06135 | 94.7598 | 0.17797 | 110.426 | 0.21824 | 131.807 | 0.23618 | 166.225 | 0.24606 | 176.68 | 0.35517 | 309.001 | 0.19298 | 293.05 | 0.32009 | 503.379 | 0.1869 | 506.915 | 0.28675 | 417.107 | 0.65236 | 559.668 | 0.66023 | 911.729 | 0.35304 | 1212.38 | 0.75491 | 1600.93 | 2.0852
128.296 | 0.069172 | 84.2127 | 0.22399 | 98.0371 | 0.27303 | 120.102 | 0.28135 | 149.507 | 0.30478 | 158.911 | 0.4386 | 280.435 | 0.2315 | 261.215 | 0.40206 | 458.676 | 0.22287 | 473.117 | 0.32983 | 392.424 | 0.74814 | 504.891 | 0.82517 | 854.352 | 0.40125 | 1146.35 | 0.87358 | 1538.16 | 2.4469
119.145 | 0.077913 | 74.8395 | 0.28276 | 89.2415 | 0.32852 | 109.218 | 0.33852 | 134.336 | 0.37638 | 148.91 | 0.50099 | 256.812 | 0.27385 | 233.771 | 0.50401 | 414.612 | 0.26951 | 433.262 | 0.39409 | 370.311 | 0.85371 | 464.213 | 0.99485 | 795.796 | 0.46572 | 1076.36 | 1.0282 | 1488.22 | 2.8006
109.655 | 0.088996 | 68.9475 | 0.33515 | 81.5606 | 0.39449 | 99.6183 | 0.40732 | 117.606 | 0.49156 | 133.532 | 0.62678 | 236.121 | 0.32169 | 209.839 | 0.63435 | 374.033 | 0.32983 | 399.552 | 0.46155 | 349.794 | 0.98299 | 424.683 | 1.209 | 743.481 | 0.5384 | 1015.71 | 1.2066 | 1438.48 | 3.2118
100.619 | 0.10247 | 62.4487 | 0.40691 | 74.5407 | 0.47276 | 92.8835 | 0.47087 | 104.412 | 0.62992 | 121.188 | 0.77016 | 219.059 | 0.373 | 187.231 | 0.80803 | 341.84 | 0.39331 | 363.342 | 0.56093 | 332.734 | 1.1116 | 400.752 | 1.3838 | 689.07 | 0.63435 | 971.987 | 1.3673 | 1394.57 | 3.7056
91.1353 | 0.12231 | 57.3599 | 0.48473 | 67.178 | 0.58382 | 84.8891 | 0.566 | 91.8674 | 0.82931 | 110.647 | 0.94161 | 200.205 | 0.44612 | 170.093 | 0.99485 | 312.418 | 0.47041 | 336.078 | 0.66288 | 314.928 | 1.2736 | 383.118 | 1.5447 | 653.5 | 0.71379 | 929.217 | 1.5649 | 1371.06 | 4.0263
83.2914 | 0.14339 | 52.1094 | 0.59621 | 61.0899 | 0.71379 | 77.8938 | 0.67763 | 85.9139 | 0.95967 | 101.529 | 1.1409 | 183.157 | 0.53304 | 155.608 | 1.2127 | 281.841 | 0.57975 | 310.86 | 0.78887 | 302.579 | 1.4188 | 364.069 | 1.7645 | 626.622 | 0.78808 | 887.442 | 1.8001 | 1345.26 | 4.3704
77.2731 | 0.16428 | 47.2922 | 0.73922 | 55.6647 | 0.86922 | 72.6277 | 0.79124 | 81.8056 | 1.0723 | 96.6741 | 1.2877 | 169.075 | 0.62803 | 145.816 | 1.4019 | 258.357 | 0.69547 | 288.976 | 0.93505 | 293.93 | 1.5309 | 349.794 | 1.9755 | 606.281 | 0.85371 | 849.241 | 2.0831 | 1319.94 | 4.8059
70.4107 | 0.19551 | 43.0063 | 0.91378 | 51.6942 | 1.0211 | 67.7176 | 0.92667 | 78.2842 | 1.1839 | 92.1434 | 1.4533 | 155.764 | 0.74516 | 139.958 | 1.5509 | 240.169 | 0.81533 | 268.901 | 1.1072 | 283.537 | 1.6885 | 336.414 | 2.2008 | 572.689 | 0.97613 | 817.575 | 2.3723 | 1287.35 | 5.4241
64.222 | 0.23243 | 39.4623 | 1.1139 | 47.7198 | 1.2212 | 64.222 | 1.05 | 75.4406 | 1.2941 | 87.1252 | 1.67 | 142.785 | 0.89659 | 134.47 | 1.7174 | 223.261 | 0.96449 | 248.227 | 1.3335 | 273.511 | 1.8717 | 321.29 | 2.4989 | 552.992 | 1.0627 | 787.878 | 2.6989 | 1255.56 | 6.1278
58.1105 | 0.28219 | 36.2829 | 1.3591 | 44.7614 | 1.4231 | 60.7244 | 1.1934 | 72.9188 | 1.4047 | 82.5452 | 1.9306 | 128.939 | 1.1251 | 128.296 | 1.9442 | 210.891 | 1.1028 | 229.831 | 1.6272 | 265.163 | 2.0439 | 311.794 | 2.7342 | 532.905 | 1.1651 | 763.828 | 3.0521 | 1225.79 | 6.9646
53.3752 | 0.33382 | 33.9655 | 1.5997 | 42.1126 | 1.6419 | 57.9944 | 1.3362 | 69.2931 | 1.5934 | 78.9919 | 2.1724 | 120.342 | 1.3163 | 124.38 | 2.1188 | 199.406 | 1.2634 | 220.598 | 1.8236 | 256.299 | 2.2611 | 300.769 | 3.0613 | 514.576 | 1.2787 | 747.208 | 3.3833 | 1191.94 | 8.0675
48.8789 | 0.40005 | 32.18 | 1.8383 | 39.5018 | 1.9268 | 55.0557 | 1.5263 | 66.6427 | 1.7645 | 75.9706 | 2.425 | 115.162 | 1.4679 | 119.264 | 2.3841 | 189.491 | 1.4345 | 211.948 | 2.0377 | 246.249 | 2.5494 | 293.05 | 3.3462 | 497.374 | 1.4047 | 733.145 | 3.7279 | 1160.19 | 9.4201
44.9858 | 0.47276 | 30.4884 | 2.1251 | 37.09 | 2.2701 | 52.266 | 1.7504 | 63.5194 | 2.0014 | 72.9188 | 2.7645 | 109.875 | 1.6435 | 113.561 | 2.7617 | 178.813 | 1.6717 | 204.045 | 2.2679 | 237.542 | 2.8629 | 287.822 | 3.5781 | 477.872 | 1.5743 | 715.759 | 4.2032 | 1115.81 | 11.8206
40.7863 | 0.57917 | 28.6842 | 2.5215 | 34.9999 | 2.6454 | 49.5185 | 2.0255 | 60.6031 | 2.2747 | 70.1998 | 3.1014 | 105.356 | 1.8273 | 109.327 | 3.0921 | 168.569 | 1.9637 | 197.619 | 2.5014 | 229.371 | 3.2279 | 280.716 | 3.9269 | 459.134 | 1.7662 | 697.389 | 4.8011 | 1080.67 | 14.4666
37.6505 | 0.69408 | 27.122 | 2.9679 | 33.2264 | 3.0582 | 47.1506 | 2.3253 | 57.4173 | 2.6667 | 68.1251 | 3.4447 | 101.022 | 2.0377 | 105.25 | 3.5073 | 160.347 | 2.2611 | 191.779 | 2.7342 | 221.704 | 3.625 | 274.059 | 4.3355 | 444.675 | 1.9559 | 682.896 | 5.3754 | 1053.99 | 17.1989
34.9649 | 0.8186 | 25.3644 | 3.6468 | 31.5428 | 3.571 | 45.3471 | 2.6218 | 55.2764 | 3.0157 | 65.5849 | 3.9465 | 98.0371 | 2.2274 | 101.732 | 3.9584 | 153.138 | 2.5673 | 184.998 | 3.0797 | 215.152 | 4.0912 | 267.56 | 4.8445 | 428.522 | 2.2008 | 671.385 | 5.9467 | 1035.19 | 19.3336
32.4385 | 0.97126 | 24.007 | 4.3835 | 29.9745 | 4.1697 | 43.6999 | 2.9501 | 53.482 | 3.3429 | 63.7103 | 4.4408 | 94.5705 | 2.4617 | 98.9234 | 4.3879 | 145.524 | 2.9857 | 180.61 | 3.3329 | 208.376 | 4.6592 | 260.954 | 5.4403 | 412.132 | 2.4889 | 652.847 | 6.9299 | 1017.74 | 20.9438
29.3222 | 1.2249 | 23.135 | 4.997 | 28.5697 | 4.8883 | 42.0284 | 3.3731 | 51.9014 | 3.6614 | 61.5805 | 5.1184 | 90.4996 | 2.7866 | 96.6741 | 4.8785 | 139.399 | 3.407 | 176.857 | 3.5997 | 202.217 | 5.3754 | 254.511 | 6.1217 | 397.559 | 2.8231 | 639.92 | 7.9315 | 1000.58 | 23.3324
27.587 | 1.4217 | 22.3616 | 5.6908 | 27.3672 | 5.7537 | 40.6235 | 3.8491 | 50.3675 | 4.1117 | 59.7008 | 6.1095 | 86.6906 | 3.1831 | 94.0988 | 5.495 | 133.666 | 3.8491 | 172.836 | 3.9703 | 197.422 | 6.0973 | 249.971 | 6.7453 | 386.195 | 3.1169 | 629.133 | 8.9071 | 985.691 | 26.3863
25.8768 | 1.665 | 21.7224 | 6.4743 | 26.5584 | 6.5198 | 39.5018 | 4.3442 | 49.1731 | 4.599 | 57.9364 | 7.3071 | 82.7932 | 3.6724 | 91.9593 | 6.2454 | 128.168 | 4.4676 | 168.232 | 4.4497 | 193.126 | 6.8199 | 246.003 | 7.4398 | 375.532 | 3.462 | 617.293 | 10.0527 | 971.987 | 30.0796
24.224 | 1.9755 | 21.1226 | 7.4771 | 25.9286 | 7.329 | 38.2195 | 5.0878 | 47.8153 | 5.269 | 56.4495 | 8.6093 | 79.5468 | 4.2032 | 89.7785 | 7.2344 | 123.636 | 5.1287 | 164.078 | 5.0271 | 189.491 | 7.6358 | 239.929 | 8.6179 | 362.616 | 3.9584 | 604.465 | 11.7147 | 960.393 | 33.0112
22.7905 | 2.3299 | 20.663 | 8.6958 | 25.5426 | 8.2717 | 37.1271 | 5.9053 | 46.5416 | 6.0973 | 54.9457 | 10.5364 | 76.3514 | 4.8251 | 87.3869 | 8.5066 | 120.463 | 5.748 | 160.347 | 5.6398 | 185.553 | 8.6958 | 234.474 | 10.1842 | 353.663 | 4.432 | 592.495 | 13.8162 | 941.376 | 38.0479
21.7224 | 2.6667 | 20.2944 | 10.2763 | 25.0869 | 9.4957 | 36.0298 | 6.9022 | 45.2113 | 7.1409 | 53.8039 | 12.464 | 74.5407 | 5.3433 | 84.8891 | 10.5893 | 117.606 | 6.3779 | 156.232 | 6.4485 | 182.608 | 9.8045 | 229.371 | 12.0835 | 343.554 | 5.0573 | 582.508 | 15.9561 | 921.813 | 44.0289
20.8082 | 3.0218 | 19.8528 | 12.5014 | 24.6394 | 10.9774 | 35.2811 | 7.8448 | 44.316 | 8.1242 | 52.7913 | 15.0119 | 73.0647 | 5.8582 | 83.0419 | 12.6397 | 115.277 | 7.1195 | 152.222 | 7.4547 | 179.53 | 11.1099 | 225.28 | 13.997 | 335.406 | 5.6851 | 570.974 | 18.9508 | 899.953 | 51.5652
19.7933 | 3.5284 | 19.4208 | 15.3458 | 24.1756 | 12.9856 | 34.5133 | 9.0779 | 43.3517 | 9.3731 | 51.9533 | 17.8115 | 71.3321 | 6.625 | 81.479 | 15.1779 | 113.221 | 7.9553 | 149.507 | 8.4388 | 176.857 | 12.539 | 221.704 | 16.1488 | 326.145 | 6.5787 | 563.036 | 22.1502 | 872.483 | 62.4177
18.9035 | 4.1158 | 19.0935 | 19.0457 | 23.8634 | 15.0871 | 33.8638 | 10.4839 | 42.4933 | 10.7278 | 51.2311 | 21.2179 | 69.5013 | 7.7048 | 79.9456 | 18.7622 | 111.201 | 8.8715 | 146.693 | 9.4484 | 174.224 | 14.3513 | 218.403 | 18.8751 | 317.775 | 7.5447 | 556.32 | 25.4788 | 850.941 | 73.1746
17.9815 | 4.8542 | 18.8092 | 23.9231 | 23.5787 | 17.4763 | 33.2597 | 12.0112 | 41.6935 | 12.464 | 50.5188 | 26.4127 | 68.057 | 8.792 | 78.913 | 22.8247 | 108.673 | 10.4212 | 144.076 | 10.5893 | 171.802 | 16.3928 | 214.722 | 22.6429 | 310.239 | 8.8096 | 549.684 | 29.249 | 829.102 | 83.7511
17.1388 | 5.8115 | 18.622 | 30.2303 | 23.2509 | 21.4526 | 32.8301 | 13.5833 | 40.9907 | 14.4521 | 49.8165 | 34.1187 | 66.6427 | 10.1842 | 77.9717 | 27.6837 | 107.162 | 11.5403 | 142.073 | 11.8561 | 169.244 | 19.0457 | 212.16 | 26.5451 | 303.792 | 10.1233 | 543.67 | 33.9146 | 807.823 | 95.1876
16.599 | 6.6382 | 18.4367 | 39.2459 | 22.9966 | 26.1761 | 32.471 | 15.7658 | 40.2595 | 17.1817 | 49.469 | 41.382 | 65.5194 | 11.6679 | 77.2731 | 34.2212 | 105.461 | 13.2083 | 139.958 | 13.3945 | 167.393 | 21.6249 | 209.211 | 31.0577 | 297.182 | 11.8088 | 539.338 | 39.2852 | 783.948 | 109.273
16.1246 | 7.5749 | 18.2533 | 49.9413 | 22.7905 | 33.4766 | 32.18 | 17.9905 | 39.5809 | 21.0278 | 49.1239 | 54.2091 | 64.415 | 13.5156 | 76.5808 | 42.5571 | 103.683 | 15.1628 | 138.15 | 15.0419 | 165.893 | 24.309 | 206.715 | 36.301 | 291.88 | 13.4751 | 532.372 | 45.0533 | 756.985 | 126.576
15.7737 | 8.4727 | 18.0898 | 65.5523 | 22.6089 | 40.6438 | 31.9875 | 20.902 | 38.9916 | 25.5043 | 48.6838 | 73.0284 | 63.3925 | 15.7343 | 76.1988 | 53.7771 | 102.242 | 17.5463 | 136.093 | 17.3544 | 164.242 | 28.2148 | 204.659 | 43.0709 | 287.822 | 15.3152 | 524.971 | 51.4108 | 732.412 | 145.162
15.5078 | 9.4673 | 17.9995 | 86.388 | 22.5187 | 48.8546 | 31.7962 | 24.6763 | 38.565 | 30.5647 | 48.2959 | 101.073 | 62.324 | 18.9508 | 75.6673 | 67.3463 | 100.82 | 20.2437 | 134.874 | 19.1604 | 162.283 | 33.4097 | 202.622 | 50.8992 | 282.405 | 17.7404 | 517.155 | 58.1978 | 701.586 | 170.008
15.3843 | 10.4839 | 17.9636 | 119.205 | 22.4288 | 59.3142 | 31.7009 | 30.1398 | 38.1431 | 38.1241 | 47.911 | 141.719 | 61.3347 | 23.1929 | 75.4406 | 89.3757 | 99.5187 | 24.019 | 133.132 | 21.9298 | 160.829 | 39.4426 | 200.807 | 60.8766 | 278.479 | 20.264 | 508.947 | 65.4868 | 681.532 | 188.077
15.2312 | 11.8679 | 17.9098 | 174.138 | 22.4512 | 73.6887 | 31.5744 | 36.301 | 37.8014 | 48.1754 | 47.6244 | 178.012 | 60.482 | 29.1614 | 75.0644 | 111.703 | 98.6271 | 27.7947 | 131.413 | 24.9493 | 159.229 | 46.6115 | 199.207 | 71.3679 | 274.608 | 23.5669 | 500.368 | 73.1015 | 664.04 | 204.558
15.0947 | 13.5021 | 17.9277 | 247.361 | 22.3393 | 91.8218 | 31.4798 | 46.8451 | 37.5753 | 61.5499 | 47.3395 | 225.619 | 60.0001 | 35.5111 | 74.8395 | 135.348 | 97.3532 | 34.5306 | 129.845 | 28.4414 | 157.96 | 56.0839 | 197.619 | 83.3334 | 270.79 | 27.2171 | 492.425 | 82.0107 | 646.351 | 225.394
14.9744 | 15.8607 | 17.9456 | 301.826 | 22.3169 | 121.613 | 31.3228 | 58.7827 | 37.3132 | 79.2692 | 47.1506 | 266.36 | 59.4625 | 43.4603 | 74.4662 | 172.061 | 96.3845 | 41.5479 | 127.912 | 33.9146 | 156.388 | 69.0512 | 196.045 | 100.268 | 266.758 | 31.6851 | 482.192 | 92.282 | 631.023 | 249.847
14.8106 | 21.1543 |  |  | 22.2723 | 149.134 | 31.1043 | 76.0088 | 37.09 | 98.1846 | 46.9623 | 303.339 | 59.1068 | 55.3042 | 74.3175 | 215.907 | 95.521 | 50.9502 | 126.134 | 40.0387 | 155.453 | 80.6283 | 195.067 | 117.079 | 263.84 | 36.0478 | 472.644 | 102.293 | 615.443 | 278.621
14.6926 | 26.8387 |  |  | 22.2946 | 181.064 | 30.9492 | 93.7704 | 36.8681 | 132.668 |  |  | 58.812 | 68.3642 | 74.169 | 256.685 | 94.5705 | 63.9978 | 124.38 | 48.9034 | 154.368 | 96.4331 | 193.706 | 140.169 | 260.693 | 41.5479 | 463.749 | 112.939 | 605.069 | 303.339
14.6047 | 33.7792 |  |  | 22.2723 | 233.656 | 30.764 | 114.76 | 36.6842 | 175.712 |  |  | 58.5187 | 83.8349 | 74.0208 | 302.733 | 93.9108 | 79.4278 | 122.774 | 60.2106 | 153.445 | 117.313 | 192.933 | 165.314 | 257.583 | 47.7915 | 451.847 | 128.876 | 593.682 | 340.649
14.5464 | 41.6311 |  |  | 22.2946 | 300.621 | 30.58 | 141.012 | 36.4648 | 224.046 |  |  | 58.3434 | 101.276 |  |  | 93.0694 | 99.4694 | 120.946 | 75.0271 | 152.527 | 147.65 | 192.355 | 195.556 | 254.765 | 55.1937 | 441.573 | 145.162 | 586.014 | 373.849
14.5174 | 53.242 |  |  |  |  | 30.3971 | 178.19 | 36.3192 | 266.36 |  |  | 58.1686 | 125.067 |  |  | 92.2356 | 124.942 | 119.742 | 92.7446 | 151.918 | 180.702 | 191.396 | 227.204 | 251.978 | 63.7423 | 430.67 | 163.506 | 578.445 | 415.238
14.5028 | 67.0775 |  |  |  |  | 30.2152 | 229.488 | 36.2829 | 301.524 |  |  | 57.9364 | 149.582 |  |  | 91.5922 | 151.691 | 118.669 | 115.567 | 151.615 | 210.366 | 190.822 | 264.767 | 249.471 | 73.5414 | 422.565 | 180.341 | 574.985 | 468.18
14.5028 | 84.5928 |  |  |  |  | 30.1247 | 270.657 |  |  |  |  | 57.7051 | 185.647 |  |  | 90.7715 | 188.077 | 117.842 | 145.598 | 151.615 | 247.114 | 190.441 | 303.339 | 247.236 | 85.0168 | 411.308 | 204.558 | 572.689 | 532.644
14.5174 | 105.409 |  |  |  |  | 30.0345 | 303.946 |  |  |  |  | 57.5323 | 221.816 |  |  | 90.4996 | 214.616 | 116.786 | 187.889 | 151.463 | 275.848 |  |  | 244.531 | 100.67 | 401.554 | 227.204 | 572.689 | 603.565
14.5028 | 136.435 | [10 empty] | 57.3026 | 260.825 |  |  | 89.9583 | 245.39 | 116.436 | 232.723 | 151.615 | 301.524 |  |  | 242.098 | 118.019 | 394.391 | 246.374
14.4884 | 172.061 | [10 empty] | 57.1881 | 301.223 |  |  | 89.6888 | 272.83 | 116.087 | 267.963 |  |  |  |  | 239.929 | 137.944 | 389.297 | 266.36
14.4884 | 220.489 | [14 empty] | 89.3307 | 303.339 | 115.855 | 307.001 |  |  |  |  | 238.017 | 159.788 | 385.038 | 287.968
14.5028 | 271.741 | [22 empty] | 236.121 | 182.883 | 381.589 | 307.616
14.4884 | 300.922 | [22 empty] | 234.474 | 214.187 | 379.685 | 329.261
[24 empty] | 233.304 | 238.853 | 375.908 | 353.489
[24 empty] | 232.605 | 268.232 | 373.285 | 382.547
[24 empty] | 231.445 | 308.849 | 372.167 | 411.929
[26 empty] | 371.052 | 463.985
[26 empty] | 370.311 | 533.71
[26 empty] | 370.681 | 605.984