## 176_24
S&C Power Fuses - Type SMU-20 (25 and 34.5 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (25 and 34.5 kV)
Very Slow Speed (TCC 176-2-4) | [9 empty] | Very Slow Speed (TCC 176-2-4)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
15993.3 | 0.02321 | 15961.3 | 0.023303 | 15993.3 | 0.023397 | 16316.4 | 0.02349 | 16105.6 | 0.032285 | 16316.4 | 0.032511 | 16332.7 | 0.032609 | 16041.3 | 0.032707
14912 | 0.023798 | 15167.7 | 0.023893 | 15182.9 | 0.023989 | 15614 | 0.024109 | 15536.1 | 0.033401 | 15850 | 0.033602 | 15567.2 | 0.034487 | 15427.8 | 0.034212
14114 | 0.024303 | 14399.1 | 0.024596 | 14399.1 | 0.024794 | 14897.1 | 0.024993 | 15046.9 | 0.034487 | 15182.9 | 0.03529 | 14941.9 | 0.03651 | 14529.3 | 0.036988
13412.3 | 0.024794 | 13710.6 | 0.025396 | 13820.7 | 0.025498 | 14085.8 | 0.025909 | 14529.3 | 0.035502 | 14529.3 | 0.03721 | 14384.8 | 0.038382 | 13848.4 | 0.039393
12593.3 | 0.025396 | 12886.4 | 0.026195 | 13199.4 | 0.026406 | 13452.6 | 0.026993 | 14043.6 | 0.036914 | 14029.6 | 0.038613 | 13655.9 | 0.040796 | 13305.4 | 0.04162
11636.8 | 0.026406 | 12233.4 | 0.026993 | 12418.3 | 0.027292 | 12834.9 | 0.028011 | 13412.3 | 0.038382 | 13398.9 | 0.040593 | 13015.9 | 0.043492 | 12543.1 | 0.044997
10763.6 | 0.027401 | 11497.9 | 0.027899 | 11860 | 0.028207 | 12307 | 0.028893 | 12809.3 | 0.040108 | 12809.3 | 0.042888 | 12331.6 | 0.046413 | 11417.7 | 0.051295
9916.23 | 0.028491 | 10763.6 | 0.029008 | 11191.7 | 0.029388 | 11695.1 | 0.030192 | 12184.5 | 0.042419 | 12160.2 | 0.045313 | 11532.5 | 0.050886 | 10497.8 | 0.057489
9062.75 | 0.029892 | 10015.8 | 0.030192 | 10424.6 | 0.030895 | 11025 | 0.031709 | 11578.7 | 0.044504 | 11475 | 0.048501 | 10677.8 | 0.055678 | 9936.08 | 0.062028
8450.05 | 0.031112 | 9338.75 | 0.031614 | 9710.16 | 0.032609 | 10248.9 | 0.033906 | 10959.1 | 0.047115 | 10904.4 | 0.051603 | 9965.93 | 0.0608 | 9460.95 | 0.066526
7894.55 | 0.032285 | 8707.4 | 0.033102 | 9026.57 | 0.034487 | 9442.05 | 0.03651 | 10331.2 | 0.049978 | 10341.5 | 0.054904 | 9310.78 | 0.066526 | 9080.89 | 0.070217
7316.8 | 0.033602 | 8175.75 | 0.034487 | 8307.62 | 0.036803 | 8812.51 | 0.038884 | 9758.83 | 0.053122 | 9788.15 | 0.058709 | 8698.69 | 0.072573 | 8672.64 | 0.075384
6842.63 | 0.034904 | 7539.63 | 0.03651 | 7585 | 0.03959 | 8224.95 | 0.041704 | 9172.16 | 0.056689 | 9218.13 | 0.063218 | 8037.94 | 0.080769 | 8175.75 | 0.081907
6148.28 | 0.037397 | 6966.92 | 0.038613 | 6911.4 | 0.043103 | 7715.05 | 0.044504 | 8534.98 | 0.060922 | 8663.97 | 0.068074 | 7405.13 | 0.090431 | 7707.34 | 0.089621
5704.03 | 0.039001 | 6580.91 | 0.040108 | 6322.87 | 0.046693 | 7200.66 | 0.047923 | 7981.87 | 0.06547 | 8192.12 | 0.072937 | 6794.9 | 0.10186 | 7186.27 | 0.099146
5297.17 | 0.041001 | 6185.28 | 0.042207 | 5755.6 | 0.050988 | 6647.05 | 0.052122 | 7524.56 | 0.069518 | 7738.23 | 0.078539 | 6259.95 | 0.11427 | 6633.77 | 0.11156
4875.26 | 0.043406 | 5755.6 | 0.044594 | 5233.99 | 0.055678 | 6099.29 | 0.057374 | 7143.29 | 0.07367 | 7287.59 | 0.08474 | 5761.36 | 0.12884 | 6129.87 | 0.12642
4536.58 | 0.045585 | 5404.18 | 0.04688 | 4698.17 | 0.061904 | 5647.27 | 0.062277 | 6457.05 | 0.081989 | 6932.17 | 0.09016 | 5307.78 | 0.14498 | 5652.92 | 0.14325
4129.57 | 0.048598 | 5104.76 | 0.049283 | 4306.7 | 0.067531 | 5265.48 | 0.067531 | 5972.54 | 0.089531 | 6521.95 | 0.09728 | 4889.91 | 0.16412 | 5244.46 | 0.16184
3781.7 | 0.05181 | 4745.39 | 0.052174 | 3885.19 | 0.074634 | 4899.69 | 0.073229 | 5647.27 | 0.094973 | 6154.43 | 0.10486 | 4504.93 | 0.18597 | 4821.92 | 0.18467
3490.95 | 0.054794 | 4473.51 | 0.054904 | 3597.26 | 0.080366 | 4424.57 | 0.0824 | 5339.72 | 0.10125 | 5848.43 | 0.11201 | 4221.43 | 0.20553 | 4442.3 | 0.21031
3251.68 | 0.057777 | 4129.57 | 0.058885 | 3330.67 | 0.086885 | 4064.02 | 0.091066 | 5084.38 | 0.10676 | 5557.64 | 0.11965 | 3932.1 | 0.22828 | 4129.57 | 0.23642
3025.79 | 0.060678 | 3846.54 | 0.062589 | 3096.19 | 0.093185 | 3770.37 | 0.099942 | 4865.52 | 0.11201 | 5329.05 | 0.12642 | 3677.28 | 0.2528 | 3912.49 | 0.25816
2829.71 | 0.06379 | 3604.46 | 0.066326 | 2927.57 | 0.099543 | 3568.6 | 0.10676 | 4688.78 | 0.11728 | 5074.22 | 0.13491 | 3418.4 | 0.28389 | 3706.81 | 0.28304
2683.64 | 0.066393 | 3397.95 | 0.069797 | 2751.57 | 0.10676 | 3337.34 | 0.1167 | 4495.93 | 0.12342 | 4826.75 | 0.14411 | 3168.23 | 0.32137 | 3511.96 | 0.31125
2542.56 | 0.069172 | 3149.28 | 0.074708 | 2570.69 | 0.11612 | 3093.1 | 0.12871 | 4280.94 | 0.13171 | 4582.17 | 0.15472 | 2954.04 | 0.35802 | 3314.06 | 0.34295
2401.69 | 0.072573 | 2986.71 | 0.078539 | 2382.55 | 0.12731 | 2918.8 | 0.13943 | 4047.8 | 0.14154 | 4354.34 | 0.1656 | 2768.13 | 0.40085 | 3105.49 | 0.38475
2252.8 | 0.077215 | 2835.37 | 0.082236 | 2217.04 | 0.13985 | 2737.85 | 0.15226 | 3827.35 | 0.15272 | 4166.9 | 0.17655 | 2638.4 | 0.43685 | 2948.14 | 0.42479
2125.85 | 0.08158 | 2670.25 | 0.087496 | 2063.02 | 0.15379 | 2575.83 | 0.16593 | 3611.68 | 0.16511 | 3947.86 | 0.18992 | 2487.24 | 0.48667 | 2718.75 | 0.49304
2002.05 | 0.087059 | 2507.22 | 0.093465 | 1885.46 | 0.17375 | 2420.98 | 0.18211 | 3374.25 | 0.18247 | 3740.33 | 0.20553 | 2347.08 | 0.54055 | 2547.65 | 0.56037
1876.06 | 0.093559 | 2351.78 | 0.10044 | 1742.24 | 0.19414 | 2286.84 | 0.19826 | 3161.9 | 0.20086 | 3547.25 | 0.2222 | 2140.79 | 0.64072 | 2384.94 | 0.63562
1750.97 | 0.10166 | 2197.18 | 0.10837 | 1609.9 | 0.21868 | 2153.67 | 0.2189 | 2968.84 | 0.22132 | 3367.51 | 0.24023 | 1964.37 | 0.75718 | 2237.08 | 0.72025
1627.71 | 0.11145 | 2048.63 | 0.11799 | 1501.06 | 0.24362 | 2022.17 | 0.24435 | 2770.9 | 0.24606 | 3142.98 | 0.26523 | 1820.61 | 0.88059 | 2090.02 | 0.82931
1505.57 | 0.12293 | 1885.46 | 0.13105 | 1354.15 | 0.28675 | 1891.13 | 0.27495 | 2583.57 | 0.27468 | 2965.88 | 0.29021 | 1675.6 | 1.0427 | 1980.15 | 0.92852
1398.18 | 0.13654 | 1752.73 | 0.14354 | 1238.84 | 0.33348 | 1782.78 | 0.30539 | 2408.91 | 0.30692 | 2829.71 | 0.31344 | 1570.15 | 1.2006 | 1887.35 | 1.0262
1315.44 | 0.1485 | 1622.83 | 0.15959 | 1117.59 | 0.39845 | 1673.93 | 0.34124 | 2225.93 | 0.34883 | 2672.92 | 0.34433 | 1477.24 | 1.3728 | 1781 | 1.164
1213.09 | 0.1676 | 1535.99 | 0.17219 | 1024.47 | 0.46387 | 1582.76 | 0.38016 | 2092.11 | 0.38514 | 2537.48 | 0.37638 | 1352.79 | 1.6468 | 1675.6 | 1.3362
1141.3 | 0.18412 | 1452.33 | 0.18634 | 958.08 | 0.52301 | 1480.19 | 0.4325 | 1960.45 | 0.42863 | 2399.29 | 0.41472 | 1248.79 | 1.952 | 1562.32 | 1.5602
1064.14 | 0.20574 | 1369.13 | 0.20348 | 892.415 | 0.5998 | 1377.36 | 0.498 | 1866.7 | 0.46947 | 2246.05 | 0.4634 | 1167.86 | 2.2838 | 1468.4 | 1.7893
1021.4 | 0.21999 | 1295.86 | 0.22043 | 814.79 | 0.72097 | 1294.56 | 0.56037 | 1761.51 | 0.52405 | 2130.11 | 0.51265 | 1085.64 | 2.7151 | 1385.65 | 2.0459
958.08 | 0.24459 | 1215.52 | 0.24313 | 764.277 | 0.82683 | 1210.67 | 0.64008 | 1673.93 | 0.57917 | 1996.05 | 0.57859 | 1017.32 | 3.199 | 1320.71 | 2.2907
912.265 | 0.26496 | 1127.69 | 0.27167 | 703.404 | 0.98299 | 1133.34 | 0.72821 | 1563.88 | 0.65892 | 1872.31 | 0.65301 | 956.165 | 3.7654 | 1247.54 | 2.6191
869.511 | 0.28876 | 1044.12 | 0.30662 | 648.674 | 1.1582 | 1047.25 | 0.85286 | 1487.61 | 0.72241 | 1775.66 | 0.72458 | 914.092 | 4.2582 | 1187.88 | 2.956
811.538 | 0.32492 | 977.434 | 0.34227 | 597.008 | 1.3755 | 975.481 | 0.982 | 1406.6 | 0.79999 | 1682.32 | 0.80239 | 863.446 | 5.0271 | 1143.59 | 3.28
756.673 | 0.36708 | 912.265 | 0.38629 | 541.819 | 1.6868 | 904.092 | 1.1466 | 1337.99 | 0.88589 | 1593.88 | 0.89033 | 823.803 | 5.7768 | 1097.65 | 3.6724
698.497 | 0.42267 | 859.999 | 0.4282 | 500.662 | 2.0094 | 837.927 | 1.3442 | 1267.66 | 0.98299 | 1522.22 | 0.97029 | 791.501 | 6.5919 | 1052.5 | 4.1241
647.378 | 0.4828 | 805.877 | 0.47895 | 470.093 | 2.3137 | 785.98 | 1.5339 | 1211.88 | 1.0723 | 1452.33 | 1.0617 | 759.706 | 7.5977 | 1012.25 | 4.6499
595.816 | 0.56149 | 749.893 | 0.5449 | 435.69 | 2.7397 | 725.551 | 1.8146 | 1158.55 | 1.1757 | 1382.89 | 1.178 | 731.378 | 8.5664 | 971.587 | 5.2166
552.764 | 0.64458 | 706.93 | 0.60704 | 407.455 | 3.215 | 680.57 | 2.0831 | 1108.68 | 1.2902 | 1322.03 | 1.289 | 702.701 | 9.7947 | 939.108 | 5.748
508.228 | 0.75491 | 667.094 | 0.67695 | 384.111 | 3.6982 | 638.378 | 2.3913 | 1054.61 | 1.4231 | 1260.08 | 1.4231 | 675.823 | 11.1099 | 906.808 | 6.4163
474.343 | 0.86662 | 625.738 | 0.76402 | 362.829 | 4.2539 | 603.612 | 2.7124 | 1007.2 | 1.5759 | 1198.62 | 1.5854 | 643.506 | 13.4616 | 880.008 | 7.0417
437.874 | 1.0139 | 577.051 | 0.89033 | 344.788 | 4.8834 | 569.598 | 3.0983 | 963.845 | 1.7295 | 1141.3 | 1.7627 | 625.738 | 15.3765 | 857.423 | 7.7279
402.193 | 1.1982 | 547.811 | 0.98989 | 325.685 | 5.7078 | 546.17 | 3.4139 | 925.127 | 1.8943 | 1081.31 | 1.9657 | 606.637 | 17.7227 | 835.417 | 8.5151
367.944 | 1.4274 | 516.426 | 1.1139 | 301.549 | 7.0206 | 524.23 | 3.7918 | 888.852 | 2.0768 | 1016.3 | 2.2543 | 592.844 | 19.8826 | 811.538 | 9.4578
338.638 | 1.6851 | 481.994 | 1.2774 | 282.007 | 8.5493 | 503.675 | 4.1906 | 853.146 | 2.2724 | 968.677 | 2.5189 | 578.785 | 22.6429 | 785.194 | 10.7708
318.598 | 1.9133 | 447.614 | 1.4827 | 267.45 | 10.2558 | 478.632 | 4.7628 | 813.162 | 2.5366 | 924.202 | 2.8175 | 565.625 | 25.8121 | 758.946 | 12.3276
295.873 | 2.2207 | 421.547 | 1.6818 | 253.644 | 12.2049 | 460.785 | 5.2637 | 774.278 | 2.8601 | 882.652 | 3.1388 | 553.317 | 29.2783 | 737.253 | 14.039
275.595 | 2.5776 | 381.05 | 2.0914 | 241.756 | 14.7294 | 436.562 | 6.0669 | 745.407 | 3.1357 | 842.127 | 3.5249 | 540.195 | 34.3584 | 716.18 | 15.829
259.027 | 2.9383 | 357.07 | 2.425 | 232.045 | 17.7049 | 420.284 | 6.752 | 718.331 | 3.4344 | 803.463 | 3.9584 | 530.559 | 39.2459 | 704.107 | 17.096
245.901 | 3.2931 | 335.604 | 2.7839 | 224.064 | 21.2604 | 401.389 | 7.6894 | 688.098 | 3.8184 | 773.504 | 4.3572 | 520.053 | 46.6115 | 687.41 | 19.0457
233.208 | 3.7316 | 318.598 | 3.1357 | 218.095 | 25.2 | 386.422 | 8.5151 | 664.431 | 4.2074 | 746.9 | 4.8251 | 509.755 | 56.0839 | 672.452 | 21.5601
222.946 | 4.1572 | 303.363 | 3.5249 | 213.136 | 30.9028 | 371.271 | 9.6104 | 635.194 | 4.7107 | 721.932 | 5.269 | 501.163 | 66.8097 | 658.478 | 24.1394
216.141 | 4.5125 | 287.129 | 4.0586 | 207.044 | 38.086 | 357.785 | 10.7386 | 607.852 | 5.2901 | 698.497 | 5.8348 | 493.208 | 81.6016 | 646.731 | 26.8656
208.29 | 4.997 | 270.949 | 4.6685 | 201.327 | 48.3684 | 342.726 | 12.3276 | 584.018 | 5.923 | 674.473 | 6.4808 | 486.351 | 97.0134 | 635.83 | 29.8996
198.926 | 5.6454 | 258.251 | 5.2743 | 197.341 | 61.4884 | 332.264 | 13.7611 | 561.118 | 6.6582 | 651.926 | 7.2199 | 480.55 | 116.728 | 625.112 | 33.7792
189.413 | 6.4679 | 245.165 | 6.1524 | 192.853 | 79.0317 | 321.8 | 15.4382 | 537.501 | 7.5901 | 627.618 | 8.0675 | 471.506 | 141.153 | 615.19 | 37.9719
181.804 | 7.329 | 231.813 | 7.2489 | 189.224 | 97.8905 | 311.666 | 17.3544 | 512.823 | 8.6871 | 600.001 | 9.2984 | 465.881 | 176.064 | 606.637 | 42.9848
173.804 | 8.3215 | 221.391 | 8.4557 | 183.265 | 127.084 | 302.757 | 19.5474 | 492.715 | 9.7947 | 578.207 | 10.8032 | 461.707 | 205.994 | 596.412 | 49.9413
166.989 | 9.3637 | 211.438 | 9.8045 | 178.919 | 168.485 | 295.282 | 21.8641 | 477.198 | 11.0214 | 556.647 | 12.4889 | 458.028 | 265.297 | 585.772 | 58.7827
160.442 | 10.6317 | 203.35 | 11.2441 | 176.784 | 215.907 | 289.435 | 24.2361 | 458.945 | 12.6018 | 538.577 | 14.4233 | 454.833 | 322.097 | 579.364 | 67.4812
154.305 | 12.1441 | 195.572 | 12.9726 | 174.327 | 278.621 | 281.162 | 28.018 | 445.827 | 14.2085 | 522.66 | 16.7575 | 453.018 | 399.356 | 571.881 | 79.9858
149.894 | 13.6378 | 189.982 | 14.6266 | 172.765 | 365.348 | 274.22 | 32.3575 | 432.218 | 16.4092 | 511.287 | 18.8751 | 451.661 | 476.207 | 563.931 | 97.4023
145.028 | 15.6715 | 184.367 | 16.8415 | 172.075 | 458.909 | 269.598 | 36.7026 | 422.391 | 18.5569 | 500.162 | 21.5386 | 451.209 | 561.636 | 557.761 | 114.531
140.602 | 17.865 | 180.175 | 19.1221 | 171.56 | 549.964 | 261.892 | 43.5908 | 412.787 | 20.9438 | 489.768 | 24.9992 | 449.858 | 602.359 | 554.979 | 130.823
137.68 | 19.5279 | 176.079 | 21.3242 | 171.217 | 604.169 | 255.681 | 51.2568 | 400.187 | 24.1394 | 481.512 | 28.1303 |  |  | 551.108 | 152.91
135.224 | 21.2391 | 171.731 | 24.7257 |  |  | 248.373 | 63.6786 | 391.87 | 27.6837 | 471.506 | 32.5848 |  |  | 547.811 | 183.984
132.811 | 23.6141 | 166.656 | 30.5036 |  |  | 243.698 | 76.3134 | 382.577 | 31.9715 | 461.707 | 38.0099 |  |  | 542.903 | 221.152
130.312 | 25.8121 | 162.054 | 37.3318 |  |  | 238.634 | 92.3744 | 376.129 | 36.0478 | 454.379 | 43.5038 |  |  | 535.891 | 276.4
127.859 | 28.6698 | 159.004 | 44.8735 |  |  | 234.846 | 108.51 | 368.681 | 42.2603 | 445.827 | 49.9912 |  |  | 532.153 | 331.574
126.208 | 31.4641 | 154.614 | 57.2168 |  |  | 231.119 | 131.479 | 360.658 | 49.8415 | 436.999 | 58.724 |  |  | 527.913 | 400.956
125.077 | 34.2212 | 151.856 | 70.3054 |  |  | 227.905 | 154.756 | 356 | 57.1596 | 430.924 | 66.7429 |  |  | 525.28 | 481.474
123.338 | 38.2386 | 150.194 | 85.614 |  |  | 225.412 | 184.721 | 351.402 | 65.03 | 425.784 | 75.4786 |  |  | 524.755 | 567.28
121.867 | 43.1571 | 148.7 | 105.409 |  |  | 223.169 | 219.829 | 346.17 | 78.795 | 420.284 | 87.7814 |  |  | 523.706 | 601.757
120.534 | 49.0504 | 145.901 | 132.27 |  |  | 220.507 | 270.657 | 342.726 | 93.5831 | 414.441 | 103.736
118.502 | 57.4462 | 144.017 | 164.654 |  |  | 218.095 | 332.238 | 339.995 | 109.273 | 409.498 | 121.979
116.855 | 67.4812 | 141.873 | 216.773 |  |  | 215.709 | 396.967 | 335.94 | 132.27 | 404.613 | 143
115.23 | 78.4804 | 140.321 | 293.492 |  |  | 214.204 | 474.78 | 333.93 | 154.756 | 401.389 | 169.161
113.514 | 93.5831 | 139.621 | 376.475 |  |  | 213.563 | 549.414 | 332.597 | 178.546 | 398.191 | 204.149
112.497 | 112.263 | 139.203 | 474.306 |  |  | 213.136 | 603.565 | 329.947 | 206.201 | 395.413 | 247.609
112.048 | 135.212 | 138.786 | 552.721 |  |  |  |  | 327.973 | 241.013 | 391.479 | 315.719
110.822 | 165.811 | 138.647 | 599.954 |  |  |  |  | 325.685 | 288.545 | 387.971 | 399.755
110.16 | 201.311 | [6 empty] | 324.061 | 363.89 | 386.036 | 496.634
109.282 | 255.916 | [6 empty] | 322.767 | 442.682 | 384.495 | 569.554
108.303 | 325.659 | [6 empty] | 322.767 | 545.582 | 382.96 | 602.961
108.086 | 409.875 | [6 empty] | 323.737 | 604.169
107.978 | 501.625
107.978 | 568.984
107.87 | 600.554