## 119_24
S&C Power Fuses - Type SMU-20 (25 and 34.5 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (25 and 34.5 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (25 and 34.5 kV)
Slow Speed (TCC 119-2-4) | [9 empty] | Slow Speed (TCC 119-2-4) | [9 empty] | Slow Speed (TCC 119-2-4)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
16251.2 | 0.016405 | 16235 | 0.016405 | 16154 | 0.016405 | 16218.8 | 0.016405 | 16202.6 | 0.016603 | 16202.6 | 0.016603 | 16381.8 | 0.024498 | 16463.9 | 0.024498 | 16513.4 | 0.024695 | 16496.8 | 0.024993 | 16563 | 0.032091 | 16398.2 | 0.032285 | 16546.4 | 0.032805
14837.7 | 0.016504 | 14912 | 0.016603 | 14971.8 | 0.016504 | 15304.8 | 0.016603 | 14912 | 0.016703 | 15335.5 | 0.016803 | 15443.2 | 0.024695 | 15723.7 | 0.024794 | 15818.3 | 0.024993 | 15881.7 | 0.025396 | 16025.3 | 0.032805 | 15881.7 | 0.033003 | 16186.4 | 0.033501
13372.1 | 0.016703 | 13094.2 | 0.016803 | 13265.5 | 0.016803 | 13793.1 | 0.016803 | 13452.6 | 0.016905 | 14399.1 | 0.017006 | 14587.6 | 0.024893 | 14456.9 | 0.025295 | 15046.9 | 0.025498 | 15304.8 | 0.025909 | 15243.7 | 0.033703 | 15304.8 | 0.033804 | 15739.4 | 0.034315
12221.2 | 0.016803 | 11907.5 | 0.017006 | 11871.8 | 0.017006 | 12480.5 | 0.017006 | 12319.3 | 0.017092 | 13412.3 | 0.017298 | 13806.9 | 0.025093 | 13574.2 | 0.025702 | 14356 | 0.025909 | 14485.8 | 0.026698 | 14704.7 | 0.034487 | 14690 | 0.034799 | 15243.7 | 0.035114
11135.8 | 0.017092 | 10341.5 | 0.017298 | 10656.5 | 0.017298 | 11147 | 0.017298 | 11169.3 | 0.017402 | 12618.6 | 0.017507 | 13068 | 0.025498 | 12669.1 | 0.026195 | 13696.9 | 0.026406 | 13724.3 | 0.027511 | 13945.7 | 0.035716 | 14213.2 | 0.035716 | 14793.2 | 0.036002
10005.8 | 0.017298 | 9071.82 | 0.017594 | 9451.49 | 0.017594 | 9946.02 | 0.0177 | 10362.2 | 0.0177 | 11718.5 | 0.017807 | 12356.3 | 0.025805 | 11836.3 | 0.026805 | 12912.2 | 0.026993 | 12938 | 0.028691 | 13252.3 | 0.036988 | 13834.5 | 0.036583 | 14284.4 | 0.037397
8707.4 | 0.017594 | 7926.19 | 0.017896 | 8315.93 | 0.017896 | 9080.89 | 0.018004 | 9594.33 | 0.018094 | 11113.6 | 0.018004 | 11555.6 | 0.026195 | 11135.8 | 0.027511 | 12099.6 | 0.027899 | 12233.4 | 0.029802 | 12631.2 | 0.038305 | 13265.5 | 0.038 | 13793.1 | 0.03869
7524.56 | 0.018004 | 6883.81 | 0.018404 | 7562.28 | 0.018294 | 8382.72 | 0.018203 | 8927.82 | 0.018404 | 10487.3 | 0.018404 | 10785.1 | 0.026698 | 10372.6 | 0.028292 | 11394.9 | 0.028893 | 11486.5 | 0.031205 | 12027.2 | 0.039789 | 12770.9 | 0.039393 | 13186.2 | 0.04039
6528.47 | 0.018404 | 6179.1 | 0.018795 | 6781.33 | 0.018795 | 7761.48 | 0.018608 | 8324.25 | 0.018908 | 9847.06 | 0.018795 | 10066 | 0.02721 | 9749.08 | 0.029212 | 10667.1 | 0.030012 | 10860.9 | 0.032511 | 11372.2 | 0.041496 | 12233.4 | 0.041001 | 12681.8 | 0.041997
5552.08 | 0.018908 | 5513.35 | 0.019309 | 5954.65 | 0.019503 | 7273.03 | 0.019003 | 7745.97 | 0.019406 | 9273.61 | 0.019098 | 9282.89 | 0.028011 | 9099.07 | 0.030192 | 9916.23 | 0.031393 | 10290 | 0.03411 | 10731.3 | 0.04358 | 11695.1 | 0.042802 | 12160.2 | 0.044018
4764.41 | 0.019503 | 5048.91 | 0.019699 | 5436.7 | 0.019997 | 6627.14 | 0.019503 | 7022.88 | 0.020198 | 8681.31 | 0.019601 | 8646.66 | 0.028806 | 8500.91 | 0.031299 | 9264.34 | 0.032707 | 9758.83 | 0.035609 | 10015.8 | 0.046506 | 11102.5 | 0.044997 | 11544 | 0.046599
4246.83 | 0.019997 | 4595.94 | 0.020198 | 4889.91 | 0.020709 | 6068.87 | 0.020097 | 6444.15 | 0.020897 | 8159.42 | 0.020097 | 7973.89 | 0.029892 | 7870.9 | 0.032707 | 8638.01 | 0.034487 | 9190.52 | 0.037584 | 9292.17 | 0.049679 | 10414.2 | 0.047923 | 10959.1 | 0.049382
3770.37 | 0.020503 | 4104.87 | 0.020792 | 4442.3 | 0.021297 | 5619.11 | 0.020709 | 5848.43 | 0.021902 | 7600.19 | 0.020792 | 7375.57 | 0.030988 | 7302.18 | 0.034384 | 8086.31 | 0.036183 | 8612.14 | 0.039789 | 8424.74 | 0.054576 | 9661.73 | 0.051914 | 10403.8 | 0.052488
3381 | 0.021001 | 3666.26 | 0.02149 | 3963.68 | 0.022211 | 5207.88 | 0.021297 | 5420.42 | 0.022705 | 7107.66 | 0.02149 | 6828.96 | 0.032285 | 6767.78 | 0.036002 | 7592.59 | 0.038114 | 8102.5 | 0.042207 | 7745.97 | 0.059418 | 8874.42 | 0.056576 | 9847.06 | 0.056125
3068.45 | 0.021598 | 3307.43 | 0.0223 | 3554.35 | 0.023094 | 4773.94 | 0.0221 | 4998.68 | 0.02349 | 6620.51 | 0.022502 | 6303.93 | 0.033703 | 6291.33 | 0.038114 | 7143.29 | 0.040108 | 7585 | 0.045087 | 7136.15 | 0.064818 | 8208.52 | 0.061719 | 9162.99 | 0.061227
2801.55 | 0.0221 | 2971.82 | 0.023002 | 3209.69 | 0.023989 | 4411.32 | 0.022796 | 4554.76 | 0.024695 | 6154.43 | 0.023397 | 5807.63 | 0.035396 | 5819.26 | 0.04039 | 6754.26 | 0.041997 | 7143.29 | 0.048019 | 6561.2 | 0.071278 | 7509.53 | 0.06821 | 8612.14 | 0.066194
2568.12 | 0.022705 | 2707.9 | 0.023798 | 2912.97 | 0.024993 | 3932.1 | 0.023989 | 4200.37 | 0.025909 | 5790.24 | 0.024303 | 5371.85 | 0.037397 | 5361.12 | 0.043103 | 6367.28 | 0.044504 | 6747.51 | 0.050784 | 5996.48 | 0.07909 | 6918.32 | 0.075308 | 8086.31 | 0.071707
2335.38 | 0.023397 | 2497.21 | 0.024596 | 2680.95 | 0.026013 | 3637.05 | 0.024893 | 3858.09 | 0.027292 | 5469.42 | 0.025295 | 5013.69 | 0.039314 | 4983.7 | 0.045998 | 5954.65 | 0.047304 | 6329.19 | 0.054576 | 5557.64 | 0.086712 | 6380.03 | 0.083312 | 7645.92 | 0.076983
2149.37 | 0.024109 | 2259.57 | 0.0256 | 2482.27 | 0.026993 | 3357.42 | 0.025909 | 3487.46 | 0.029506 | 5135.48 | 0.026406 | 4674.74 | 0.041413 | 4577.59 | 0.04958 | 5529.92 | 0.050784 | 5924.95 | 0.058826 | 5181.91 | 0.094499 | 5825.08 | 0.093559 | 7107.66 | 0.084995
1976.19 | 0.024893 | 2125.85 | 0.0263 | 2307.52 | 0.028095 | 3093.1 | 0.027101 | 3241.94 | 0.031205 | 4826.75 | 0.027704 | 4285.22 | 0.044504 | 4238.35 | 0.053602 | 5197.48 | 0.053979 | 5524.39 | 0.063598 | 4797.87 | 0.10361 | 5371.85 | 0.10361 | 6754.26 | 0.091615
1816.97 | 0.025702 | 1984.11 | 0.027292 | 2160.14 | 0.029212 | 2795.95 | 0.028893 | 2956.99 | 0.033703 | 4500.43 | 0.0293 | 3939.97 | 0.047684 | 3916.4 | 0.057777 | 4846.09 | 0.058125 | 5013.69 | 0.071278 | 4477.98 | 0.11336 | 4855.8 | 0.11858 | 6285.04 | 0.10145
1673.93 | 0.026591 | 1855.53 | 0.028207 | 2052.73 | 0.030102 | 2583.57 | 0.030404 | 2675.6 | 0.036803 | 4204.57 | 0.031112 | 3633.41 | 0.05109 | 3557.91 | 0.063598 | 4536.58 | 0.062277 | 4646.77 | 0.078303 | 4171.07 | 0.12516 | 4345.64 | 0.1375 | 5924.95 | 0.11078
1542.14 | 0.027704 | 1737.02 | 0.029388 | 1927.4 | 0.031393 | 2377.79 | 0.032285 | 2457.57 | 0.039789 | 3951.81 | 0.032904 | 3327.34 | 0.05529 | 3294.23 | 0.069033 | 4212.99 | 0.067531 | 4259.59 | 0.087408 | 3881.31 | 0.13846 | 3955.76 | 0.15705 | 5552.08 | 0.1217
1420.73 | 0.028893 | 1622.83 | 0.03071 | 1789.92 | 0.033201 | 2155.82 | 0.034904 | 2225.93 | 0.043711 | 3669.93 | 0.03529 | 3105.49 | 0.058826 | 3004.69 | 0.076523 | 3943.91 | 0.072428 | 3971.62 | 0.095736 | 3622.53 | 0.15272 | 3717.95 | 0.17202 | 5223.53 | 0.1329
1318.07 | 0.030192 | 1528.32 | 0.032091 | 1670.58 | 0.034904 | 1998.05 | 0.03721 | 2050.68 | 0.047493 | 3435.54 | 0.037584 | 2875.35 | 0.063281 | 2779.23 | 0.083562 | 3684.64 | 0.078225 | 3706.81 | 0.10444 | 3438.97 | 0.16577 | 3508.45 | 0.18803 | 4885.02 | 0.14629
1205.83 | 0.031804 | 1429.28 | 0.033804 | 1554.53 | 0.036914 | 1853.68 | 0.039709 | 1893.02 | 0.051707 | 3171.4 | 0.040715 | 2678.27 | 0.06821 | 2609.54 | 0.090341 | 3452.76 | 0.084233 | 3490.95 | 0.11257 | 3219.33 | 0.18211 | 3347.36 | 0.20166 | 4637.49 | 0.15784
1119.82 | 0.033401 | 1335.32 | 0.035609 | 1437.88 | 0.039511 | 1699.23 | 0.043103 | 1761.51 | 0.055678 | 2951.09 | 0.044018 | 2499.71 | 0.073083 | 2416.14 | 0.098553 | 3235.47 | 0.090794 | 3320.69 | 0.12122 | 3044 | 0.19965 | 3165.06 | 0.22065 | 4433.43 | 0.16912
1034.76 | 0.035609 | 1237.6 | 0.038 | 1348.74 | 0.04162 | 1545.23 | 0.047115 | 1614.74 | 0.061472 | 2710.61 | 0.048115 | 2321.41 | 0.079169 | 2201.57 | 0.11056 | 3034.88 | 0.098061 | 3117.94 | 0.13158 | 2863.87 | 0.22021 | 2977.76 | 0.24289 | 4187.79 | 0.18467
957.122 | 0.037886 | 1126.56 | 0.041413 | 1253.79 | 0.044504 | 1415.06 | 0.051707 | 1477.24 | 0.068006 | 2514.75 | 0.052279 | 2145.07 | 0.085677 | 2006.06 | 0.12454 | 2866.73 | 0.10591 | 2974.79 | 0.14069 | 2705.19 | 0.23975 | 2824.05 | 0.26496 | 3987.53 | 0.19946
872.123 | 0.041001 | 1005.18 | 0.046321 | 1156.24 | 0.048019 | 1298.45 | 0.056407 | 1360.93 | 0.074634 | 2321.41 | 0.057317 | 2002.05 | 0.092906 | 1837.07 | 0.13943 | 2713.32 | 0.1137 | 2832.54 | 0.15074 | 2550.2 | 0.2647 | 2680.95 | 0.28934 | 3793.06 | 0.21693
786.766 | 0.045087 | 936.295 | 0.049679 | 1064.14 | 0.052122 | 1179.6 | 0.062589 | 1250.04 | 0.082813 | 2127.98 | 0.063471 | 1840.75 | 0.10288 | 1689.06 | 0.1558 | 2534.95 | 0.12529 | 2705.19 | 0.16216 | 2396.89 | 0.29312 | 2555.31 | 0.3125 | 3611.68 | 0.23547
686.037 | 0.051192 | 854 | 0.054904 | 979.391 | 0.056407 | 1085.64 | 0.069033 | 1155.08 | 0.091066 | 1925.47 | 0.071923 | 1723.18 | 0.11145 | 1560.76 | 0.17497 | 2373.04 | 0.13736 | 2588.74 | 0.17392 | 2277.71 | 0.31785 | 2413.73 | 0.34398 | 3438.97 | 0.25636
608.46 | 0.057489 | 785.194 | 0.060075 | 902.285 | 0.061411 | 973.532 | 0.078303 | 1069.48 | 0.099942 | 1738.76 | 0.081417 | 1593.88 | 0.12367 | 1452.33 | 0.1959 | 2230.38 | 0.15044 | 2467.42 | 0.18878 | 2136.51 | 0.35375 | 2307.52 | 0.37189 | 3277.8 | 0.27661
537.501 | 0.065404 | 716.18 | 0.066526 | 831.25 | 0.066993 | 894.201 | 0.086539 | 992.206 | 0.11056 | 1593.88 | 0.090703 | 1486.13 | 0.13572 | 1332.65 | 0.22444 | 2108.91 | 0.16445 | 2356.49 | 0.20369 | 2018.13 | 0.39292 | 2190.59 | 0.40529 | 3108.6 | 0.30448
490.748 | 0.072937 | 658.478 | 0.073375 | 775.053 | 0.072428 | 831.25 | 0.094688 | 926.979 | 0.12219 | 1442.2 | 0.1034 | 1393.99 | 0.1485 | 1257.56 | 0.24631 | 1992.07 | 0.17922 | 2234.85 | 0.22287 | 1898.71 | 0.43685 | 2087.93 | 0.44212 | 2971.82 | 0.32885
436.999 | 0.084065 | 605.425 | 0.081417 | 709.053 | 0.079566 | 735.044 | 0.1099 | 864.309 | 0.13558 | 1319.39 | 0.1167 | 1308.88 | 0.16265 | 1185.51 | 0.27113 | 1879.81 | 0.19668 | 2136.51 | 0.23927 | 1793.51 | 0.48231 | 1992.07 | 0.47895 | 2790.37 | 0.36416
397.395 | 0.095736 | 554.979 | 0.090703 | 657.162 | 0.086539 | 654.539 | 0.12718 | 802.66 | 0.15165 | 1220.39 | 0.13027 | 1217.95 | 0.18011 | 1107.57 | 0.30662 | 1757.99 | 0.21977 | 2028.25 | 0.2605 | 1704.33 | 0.53038 | 1896.81 | 0.52721 | 2664.92 | 0.39686
356.713 | 0.11167 | 512.311 | 0.10044 | 604.82 | 0.095927 | 597.606 | 0.14311 | 743.918 | 0.17271 | 1141.3 | 0.14382 | 1147.02 | 0.19708 | 1036.83 | 0.34398 | 1650.66 | 0.2441 | 1940.94 | 0.28304 | 1608.29 | 0.58969 | 1804.3 | 0.57801 | 2527.35 | 0.43554
324.385 | 0.1291 | 481.031 | 0.10914 | 564.495 | 0.10507 | 562.804 | 0.15596 | 693.625 | 0.19434 | 1068.41 | 0.15879 | 1075.91 | 0.21824 | 965.775 | 0.39056 | 1542.14 | 0.27276 | 1855.53 | 0.3057 | 1504.07 | 0.67425 | 1699.23 | 0.64781 | 2384.94 | 0.48376
284.272 | 0.15847 | 451.209 | 0.11882 | 522.138 | 0.11682 | 513.336 | 0.1785 | 640.937 | 0.22243 | 995.187 | 0.17584 | 1010.22 | 0.24047 | 895.096 | 0.44746 | 1420.73 | 0.31501 | 1757.99 | 0.3365 | 1412.23 | 0.76785 | 1603.47 | 0.72821 | 2268.62 | 0.53038
252.631 | 0.19414 | 421.126 | 0.13001 | 483.442 | 0.12936 | 472.922 | 0.20308 | 582.851 | 0.26259 | 936.295 | 0.19434 | 945.705 | 0.26789 | 846.348 | 0.49551 | 1326.01 | 0.35802 | 1665.58 | 0.37077 | 1319.39 | 0.87883 | 1511.61 | 0.82188 | 2162.3 | 0.57801
226.542 | 0.23336 | 391.479 | 0.14411 | 448.959 | 0.14411 | 437.436 | 0.23127 | 535.356 | 0.3057 | 880.888 | 0.21564 | 882.652 | 0.30084 | 787.553 | 0.5677 | 1241.32 | 0.40326 | 1589.11 | 0.40448 | 1219.17 | 1.0221 | 1425 | 0.93038 | 2042.5 | 0.63944
201.932 | 0.28761 | 364.283 | 0.16071 | 411.55 | 0.16379 | 405.018 | 0.26576 | 490.258 | 0.35874 | 829.589 | 0.23808 | 806.683 | 0.34988 | 735.78 | 0.64458 | 1174.89 | 0.44926 | 1519.18 | 0.44124 | 1149.32 | 1.157 | 1355.5 | 1.0293 | 1939 | 0.70528
182.716 | 0.34467 | 342.726 | 0.17619 | 384.111 | 0.18357 | 373.879 | 0.3057 | 444.047 | 0.43598 | 743.175 | 0.28589 | 746.153 | 0.40045 | 683.298 | 0.74516 | 1096.55 | 0.51111 | 1461.07 | 0.47751 | 1085.64 | 1.3019 | 1279.12 | 1.1675 | 1838.91 | 0.7818
166.157 | 0.41265 | 320.836 | 0.19629 | 358.143 | 0.20471 | 347.906 | 0.34814 | 405.423 | 0.51625 | 680.57 | 0.33348 | 683.982 | 0.46853 | 633.925 | 0.86662 | 1037.87 | 0.5643 | 1385.65 | 0.52773 | 1029.6 | 1.4767 | 1213.09 | 1.3124 | 1737.02 | 0.87445
150.947 | 0.497 | 303.363 | 0.21499 | 334.264 | 0.22966 | 317.962 | 0.41265 | 369.05 | 0.61806 | 620.131 | 0.39292 | 633.292 | 0.54109 | 594.031 | 0.98989 | 984.3 | 0.62803 | 1323.36 | 0.58207 | 969.646 | 1.6936 | 1148.17 | 1.4797 | 1660.59 | 0.95393
138.647 | 0.59146 | 282.289 | 0.24289 | 311.354 | 0.26024 | 294.103 | 0.47751 | 336.949 | 0.74218 | 566.191 | 0.46155 | 592.251 | 0.61375 | 554.425 | 1.1318 | 941.93 | 0.69339 | 1274.01 | 0.62741 | 919.593 | 1.9364 | 1095.46 | 1.66 | 1554.53 | 1.0984
125.202 | 0.72169 | 261.368 | 0.27744 | 288.857 | 0.29755 | 273.399 | 0.54653 | 307.64 | 0.8948 | 525.28 | 0.52985 | 554.425 | 0.69617 | 516.426 | 1.2993 | 895.096 | 0.77093 | 1215.52 | 0.69062 | 855.709 | 2.3045 | 1046.21 | 1.8568 | 1483.16 | 1.2175
111.936 | 0.90741 | 241.515 | 0.31977 | 267.985 | 0.33886 | 251.875 | 0.642 | 282.854 | 1.0638 | 480.07 | 0.6249 | 521.094 | 0.78729 | 475.768 | 1.5401 | 848.043 | 0.86316 | 1164.36 | 0.75718 | 816.422 | 2.6165 | 1004.18 | 2.0562 | 1403.78 | 1.3728
98.4879 | 1.1839 | 224.512 | 0.36452 | 245.41 | 0.39885 | 233.208 | 0.75114 | 248.373 | 1.4019 | 431.355 | 0.75869 | 481.031 | 0.92389 | 446.72 | 1.7715 | 802.66 | 0.96738 | 1107.57 | 0.84606 | 778.159 | 2.9738 | 963.845 | 2.2747 | 1340.67 | 1.5309
83.5073 | 1.67 | 208.082 | 0.41888 | 226.316 | 0.4634 | 215.925 | 0.88059 | 226.542 | 1.7038 | 376.505 | 0.98989 | 444.492 | 1.0896 | 419.864 | 2.0582 | 742.432 | 1.1443 | 1054.61 | 0.94256 | 742.432 | 3.3934 | 933.491 | 2.4765 | 1281.68 | 1.7174
75.0334 | 2.0789 | 189.035 | 0.503 | 206.63 | 0.54927 | 193.046 | 1.1028 | 208.29 | 2.0459 | 335.268 | 1.2421 | 407.455 | 1.3006 | 395.809 | 2.3865 | 691.547 | 1.3282 | 993.199 | 1.0788 | 712.608 | 3.8032 | 900.483 | 2.7342 | 1225.28 | 1.9152
68.9191 | 2.4889 | 174.501 | 0.59028 | 188.468 | 0.6576 | 178.74 | 1.298 | 185.292 | 2.6854 | 305.189 | 1.4901 | 375.377 | 1.554 | 372.014 | 2.7755 | 648.674 | 1.5202 | 932.557 | 1.2249 | 687.41 | 4.2412 | 866.04 | 3.0248 | 1173.71 | 2.1465
64.4528 | 2.9207 | 161.246 | 0.68718 | 174.327 | 0.76708 | 164.503 | 1.5556 | 172.075 | 3.199 | 285.411 | 1.7243 | 349.649 | 1.8475 | 350.7 | 3.2376 | 602.406 | 1.7822 | 866.906 | 1.4432 | 665.096 | 4.6919 | 831.25 | 3.4207 | 1126.56 | 2.3961
61.0037 | 3.3462 | 150.495 | 0.78729 | 161.085 | 0.90469 | 151.704 | 1.8623 | 161.246 | 3.8032 | 268.253 | 1.9657 | 331.601 | 2.0977 | 331.269 | 3.7616 | 568.46 | 2.0377 | 817.238 | 1.665 | 646.731 | 5.1647 | 798.656 | 3.8376 | 1079.15 | 2.6854
57.5086 | 3.8645 | 138.924 | 0.92112 | 151.552 | 1.0303 | 140.883 | 2.2252 | 152.312 | 4.4364 | 252.631 | 2.2611 | 312.915 | 2.425 | 311.043 | 4.5034 | 535.891 | 2.3299 | 770.416 | 1.9114 | 630.133 | 5.6851 | 771.187 | 4.3355 | 1036.83 | 3.0097
54.54 | 4.4497 | 129.792 | 1.0553 | 140.883 | 1.2042 | 132.281 | 2.5983 | 146.047 | 4.9523 | 237.919 | 2.6113 | 297.654 | 2.7452 | 297.654 | 5.0624 | 513.85 | 2.5698 | 737.253 | 2.1444 | 615.805 | 6.2767 | 745.407 | 4.8155 | 997.179 | 3.3968
51.6213 | 5.201 | 121.745 | 1.203 | 131.358 | 1.3977 | 124.952 | 3.0187 | 140.04 | 5.5392 | 227.223 | 2.9501 | 283.42 | 3.1169 | 287.704 | 5.6173 | 489.278 | 2.9207 | 704.107 | 2.4153 | 601.202 | 6.9716 | 721.932 | 5.3862 | 960.958 | 3.8261
49.0546 | 6.0245 | 113.401 | 1.4075 | 122.478 | 1.6304 | 116.855 | 3.5961 | 134.684 | 6.1401 | 215.494 | 3.4104 | 272.58 | 3.4863 | 278.922 | 6.2205 | 466.814 | 3.2604 | 673.798 | 2.7369 | 591.659 | 7.5977 | 698.497 | 6.1278 | 928.835 | 4.2752
46.6155 | 6.9995 | 105.946 | 1.6386 | 115.576 | 1.8717 | 110.27 | 4.2369 | 128.372 | 7.2055 | 206.424 | 3.8299 | 261.63 | 3.9151 | 271.492 | 6.8472 | 444.047 | 3.665 | 641.578 | 3.1545 | 581.686 | 8.3716 | 681.251 | 6.7995 | 896.888 | 4.8396
44.5198 | 8.0998 | 98.9816 | 1.9114 | 106.264 | 2.2633 | 104.264 | 4.9821 | 124.205 | 8.1812 | 197.538 | 4.3269 | 253.137 | 4.3096 | 265.319 | 7.4547 | 427.49 | 4.0465 | 621.373 | 3.5284 | 568.46 | 9.5912 | 664.431 | 7.6281 | 869.511 | 5.3594
42.6034 | 9.345 | 93.8721 | 2.153 | 99.279 | 2.6507 | 99.9763 | 5.6511 | 120.413 | 9.2336 | 188.846 | 4.9523 | 244.186 | 4.8107 | 259.545 | 8.247 | 410.317 | 4.4765 | 598.802 | 3.9862 | 556.647 | 10.8248 | 648.026 | 8.5322 | 842.97 | 6.1095
40.9739 | 10.8682 | 88.4055 | 2.4715 | 93.3106 | 3.1263 | 96.0562 | 6.442 | 117.323 | 10.463 | 181.26 | 5.6285 | 233.675 | 5.5447 | 254.152 | 9.0598 | 396.998 | 4.903 | 579.944 | 4.481 | 546.17 | 12.0956 | 635.83 | 9.3357 | 822.157 | 6.8063
39.8027 | 12.6018 | 83.0908 | 2.8946 | 87.2636 | 3.7391 | 92.8452 | 7.2344 | 114.541 | 11.6913 | 174.327 | 6.4099 | 225.638 | 6.2704 | 248.621 | 9.9031 | 384.88 | 5.3916 | 561.679 | 4.992 | 535.356 | 13.5969 | 622.617 | 10.4839 | 801.857 | 7.6358
38.665 | 14.612 | 77.7839 | 3.4104 | 82.5112 | 4.3791 | 90.2816 | 8.0675 | 112.385 | 12.8564 | 168.162 | 7.329 | 217.877 | 7.1409 | 245.165 | 10.8032 | 371.271 | 5.9171 | 545.079 | 5.5948 | 525.28 | 15.1931 | 610.899 | 11.6679 | 778.938 | 8.6871
37.5974 | 17.5814 | 73.3274 | 3.9942 | 78.3302 | 5.1235 | 87.7888 | 9.1417 | 110.049 | 14.3944 | 161.569 | 8.4052 | 210.383 | 8.1486 | 241.515 | 11.6913 | 358.86 | 6.5459 | 528.97 | 6.3525 | 515.394 | 17.3891 | 599.401 | 12.9338 | 762.75 | 9.7361
36.7058 | 20.902 | 69.0571 | 4.6966 | 75.3342 | 5.8115 | 85.8785 | 10.1944 | 107.332 | 16.8246 | 156.637 | 9.4013 | 203.758 | 9.2151 | 237.681 | 12.6271 | 346.863 | 7.2344 | 513.85 | 7.1624 | 505.694 | 19.5279 | 588.12 | 14.6852 | 748.395 | 10.9665
35.8712 | 25.5553 | 65.9524 | 5.397 | 72.3803 | 6.7791 | 83.842 | 11.5865 | 105.523 | 19.567 | 152.77 | 10.7064 | 197.341 | 10.4839 | 234.377 | 13.5969 | 335.268 | 8.0917 | 503.675 | 7.9236 | 496.673 | 22.0838 | 579.364 | 16.5576 | 732.11 | 12.3523
35.2313 | 31.1199 | 62.8615 | 6.1894 | 70.2411 | 7.6358 | 82.264 | 12.9079 | 103.641 | 22.3504 | 149.445 | 12.0232 | 192.084 | 11.6213 | 231.119 | 14.6852 | 325.36 | 9.0961 | 491.731 | 8.8449 | 490.748 | 24.7257 | 571.881 | 18.8562 | 718.331 | 13.8162
34.6721 | 38.0099 | 59.8555 | 7.2561 | 68.5069 | 8.5066 | 80.7158 | 14.6999 | 101.894 | 25.2252 | 145.61 | 13.7748 | 187.341 | 13.1951 | 227.678 | 16.1973 | 315.744 | 10.2763 | 480.07 | 9.8438 | 483.926 | 28.018 | 561.118 | 21.7116 | 706.223 | 15.3458
34.2928 | 47.5056 | 57.5086 | 8.3968 | 66.6153 | 9.6876 | 79.1175 | 17.096 | 100.377 | 28.929 | 142.299 | 15.5622 | 183.815 | 14.7441 | 224.512 | 17.5463 | 307.333 | 11.6213 | 470.564 | 11.1099 | 475.293 | 32.4223 | 554.425 | 25.1245 | 694.319 | 17.2333
33.9176 | 58.5481 | 55.4751 | 9.62 | 65.0355 | 10.89 | 78.1737 | 19.567 | 99.3783 | 32.8137 | 139.063 | 17.5463 | 179.995 | 16.7073 | 220.949 | 19.6454 | 301.549 | 12.8693 | 461.246 | 12.4391 | 467.749 | 38.5844 | 546.17 | 29.1322 | 683.298 | 19.2372
33.7822 | 77.7773 | 53.6206 | 11.0988 | 63.8754 | 12.0956 | 76.856 | 22.6429 | 98.2911 | 38.2769 | 135.901 | 20.4267 | 176.784 | 18.6313 | 218.095 | 21.474 | 295.578 | 14.3944 | 453.018 | 14.1801 | 459.864 | 45.6885 | 536.964 | 34.3241 | 672.452 | 21.5386
33.7484 | 99.6685 | 52.2445 | 12.6903 | 62.548 | 13.5697 | 75.7118 | 26.5451 | 97.3131 | 45.0533 | 133.344 | 23.1697 | 173.804 | 20.8602 | 215.709 | 23.7325 | 289.435 | 16.1488 | 444.936 | 15.8765 | 454.833 | 53.242 | 528.97 | 41.2168 | 659.137 | 24.7257
33.7147 | 137.806 | 50.9036 | 14.612 | 61.5552 | 15.2998 | 74.7339 | 30.8719 | 96.1523 | 53.0825 | 131.621 | 26.6249 | 170.704 | 23.3324 | 213.349 | 26.3599 | 283.988 | 17.9905 | 436.126 | 18.1531 | 448.51 | 62.7305 | 520.574 | 49.247 | 646.731 | 28.4983
33.6473 | 183.066 | 49.796 | 17.1817 | 60.5781 | 17.4763 | 73.4007 | 37.22 | 95.6728 | 61.9203 | 130.182 | 30.3515 | 169.005 | 26.1238 | 210.594 | 29.6021 | 279.201 | 19.8826 | 429.203 | 20.4676 | 442.275 | 72.8097 | 513.85 | 58.0816 | 637.103 | 31.9715
33.6137 | 250.598 | 48.7612 | 19.6454 | 59.8555 | 19.7242 | 72.5252 | 44.1171 | 94.4371 | 73.984 | 128.372 | 35.4048 | 167.491 | 29.1906 | 207.874 | 33.2098 | 274.494 | 22.3058 | 423.237 | 23.0772 | 435.255 | 90.274 | 507.213 | 70.5166 | 625.112 | 37.1085
33.6137 | 470.527 | 48.0833 | 23.2393 | 58.9644 | 23.3558 | 71.5885 | 55.9159 | 93.591 | 90.1838 | 126.334 | 41.7144 | 165.328 | 32.8137 | 206.011 | 37.6317 | 270.408 | 24.7505 | 416.935 | 26.4391 | 427.49 | 117.079 | 500.662 | 83.0007 | 617.038 | 42.4296
33.6137 | 561.636 | 47.3674 | 27.962 | 58.1447 | 27.934 | 70.8761 | 70.5872 | 92.1054 | 113.846 | 124.702 | 49.1486 | 163.683 | 36.9604 | 203.554 | 42.1337 | 266.382 | 27.6837 | 409.498 | 30.7179 | 420.705 | 150.784 | 495.185 | 98.6768 | 609.069 | 48.6595
33.513 | 601.757 | 46.8492 | 32.4547 | 57.5086 | 32.7809 | 69.6814 | 88.6636 | 91.2802 | 146.767 | 122.846 | 58.6066 | 161.569 | 43.0278 | 201.126 | 48.1754 | 261.63 | 31.9077 | 402.998 | 35.5467 | 413.613 | 204.558 | 488.301 | 120.403 | 601.804 | 55.5814
|  | 46.1517 | 38.7003 | 56.6524 | 40.6032 | 68.9191 | 113.505 | 90.2816 | 187.326 | 121.017 | 70.1649 | 159.641 | 50.4937 | 198.926 | 54.6445 | 258.251 | 36.1923 | 396.205 | 42.3872 | 406.641 | 284.818 | 482.959 | 146.767 | 595.816 | 65.1602
|  | 45.6468 | 46.1939 | 56.0887 | 49.9413 | 67.961 | 157.724 | 89.7415 | 244.655 | 119.096 | 87.6936 | 157.895 | 59.8504 | 196.749 | 63.1712 | 254.152 | 42.0916 | 389.526 | 49.3456 | 401.389 | 383.696 | 477.198 | 192.068 | 589.297 | 74.2063
|  | 45.4192 | 54.6991 | 56.0326 | 61.1206 | 67.4869 | 212.056 | 89.3833 | 314.144 | 117.558 | 107.753 | 155.856 | 73.1015 | 194.597 | 72.8097 | 249.868 | 49.9413 | 382.96 | 59.6711 | 398.191 | 519.493 | 472.922 | 248.105 | 581.686 | 87.9571
|  | 45.1023 | 64.7056 | 55.9207 | 76.8495 | 67.3521 | 602.961 | 89.3833 | 398.956 | 115.923 | 135.89 | 154.614 | 85.8713 | 192.468 | 84.5083 | 246.64 | 59.3142 | 378.014 | 72.5916 | 396.998 | 604.169 | 470.564 | 308.849 | 575.323 | 106.149
|  | 44.9223 | 80.9514 | 55.7532 | 100.068 |  |  | 89.3833 | 497.131 | 114.541 | 166.476 | 152.922 | 104.151 | 189.982 | 96.1442 | 242.968 | 71.7974 | 371.271 | 91.5467 |  |  | 469.623 | 379.879 | 567.324 | 132.403
|  | 44.6089 | 104.778 | 55.5861 | 131.085 |  |  | 89.2939 | 575.278 | 113.061 | 226.977 | 150.947 | 135.619 | 188.092 | 110.702 | 238.395 | 89.1972 | 363.192 | 120.765 |  |  | 468.217 | 467.712 | 561.118 | 163.016
|  | 44.4753 | 138.22 | 55.4196 | 181.064 |  |  | 89.2939 | 604.169 | 112.385 | 300.922 | 149.147 | 176.947 | 185.292 | 141.861 | 233.675 | 113.165 | 355.644 | 163.669 |  |  | 467.281 | 561.074 | 555.535 | 207.234
|  | 44.4753 | 241.254 | 55.3642 | 250.097 |  |  |  |  | 111.936 | 393.41 | 147.515 | 241.979 | 183.081 | 179.801 | 229.966 | 142.572 | 349.999 | 214.187 |  |  | 466.814 | 602.961 | 551.108 | 257.714
|  | 44.4753 | 598.755 | 55.3089 | 473.358 |  |  |  |  | 111.713 | 604.169 | 146.193 | 337.934 | 181.079 | 236.24 | 226.542 | 186.765 | 344.1 | 279.458 |  |  |  |  | 546.717 | 318.254
|  |  |  | 55.2536 | 601.155 | [6 empty] | 145.319 | 456.164 | 179.456 | 307.308 | 223.616 | 244.166 | 339.995 | 373.475 |  |  |  |  | 543.446 | 401.357
[12 empty] | 145.028 | 553.827 | 178.204 | 402.563 | 221.834 | 299.721 | 336.276 | 485.341 |  |  |  |  | 541.819 | 490.71
[12 empty] | 144.884 | 605.984 | 177.138 | 500.623 | 220.067 | 377.984 | 334.264 | 558.834 |  |  |  |  | 540.195 | 566.713
[14 empty] | 176.255 | 565.581 | 218.969 | 459.368 | 332.93 | 602.961 |  |  |  |  | 539.116 | 598.755
[14 empty] | 175.727 | 607.197 | 218.313 | 552.721
[16 empty] | 217.877 | 603.565