## 176_152
S&C Power Fuses - Type SMD-2C (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-2C (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-2C (34.5 and 46 kV)
Very Slow Speed (TCC 176-1-5-2) | [9 empty] | Very Slow Speed (TCC 176-1-5-2) | [9 empty] | Very Slow Speed (TCC 176-1-5-2)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 2-200E |  | 2-250E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
42998.7 | 0.016405 | 42998.7 | 0.016504 | 42998.7 | 0.016603 | 42998.7 | 0.016803 | 43076.5 | 0.01756 | 43101.2 | 0.028541 | 43101.2 | 0.028953 | 43076.5 | 0.029743 | 43101.2 | 0.030765 | 43051.8 | 0.033239 | 43076.5 | 0.034559 | 43076.5 | 0.039335
41519.8 | 0.016703 | 41106.7 | 0.016803 | 41147.8 | 0.016888 | 40819.9 | 0.017194 | 39847.5 | 0.018143 | 38501 | 0.030051 | 33747.7 | 0.032804 | 38567.3 | 0.031352 | 38281.1 | 0.032898 | 40237.5 | 0.035057 | 40007.6 | 0.036848 | 40007.6 | 0.042351
40091.7 | 0.016989 | 39692.8 | 0.017092 | 39692.8 | 0.017194 | 39376.5 | 0.017489 | 33612.7 | 0.019816 | 31361.4 | 0.033106 | 26959.3 | 0.037018 | 33134.7 | 0.033853 | 33516.5 | 0.035726 | 34868 | 0.039088 | 34848 | 0.041701 | 33922.2 | 0.049718
38674.1 | 0.017298 | 38251 | 0.017402 | 38289.3 | 0.017489 | 37946.2 | 0.017896 | 28565.3 | 0.02152 | 26123 | 0.036345 | 21548.7 | 0.041869 | 28078.5 | 0.037081 | 28778.9 | 0.039267 | 29345 | 0.04508 | 29785.3 | 0.048094 | 29615.2 | 0.057209
37232.1 | 0.017594 | 36824.7 | 0.0177 | 36861.6 | 0.017789 | 36494.8 | 0.018203 | 24924.2 | 0.02325 | 22276.8 | 0.039493 | 17593 | 0.047464 | 23834.9 | 0.040874 | 24739.2 | 0.043507 | 24513.5 | 0.052831 | 25766.3 | 0.05515 | 25751.5 | 0.066586
35808 | 0.017896 | 35380.8 | 0.018004 | 35416.2 | 0.018203 | 35098.9 | 0.018608 | 21909.7 | 0.02499 | 18271 | 0.043958 | 15306.6 | 0.051901 | 20536.2 | 0.044668 | 21145.1 | 0.048481 | 19876.4 | 0.064226 | 21847.1 | 0.065264 | 21859.6 | 0.080532
34369.5 | 0.018203 | 33959.5 | 0.018404 | 33993.5 | 0.018497 | 33655.3 | 0.019003 | 18910 | 0.027294 | 15332.9 | 0.048899 | 13135.4 | 0.057669 | 16785.6 | 0.051017 | 18386.5 | 0.0539 | 16824.1 | 0.076881 | 18397 | 0.078438 | 18888.3 | 0.097344
32955.9 | 0.018608 | 32530.2 | 0.018795 | 32562.8 | 0.018908 | 32206.6 | 0.019406 | 16125.8 | 0.030103 | 12882 | 0.054772 | 11086.5 | 0.066168 | 14831.8 | 0.055977 | 15805.6 | 0.061139 | 14322.4 | 0.093358 | 15554.1 | 0.097065 | 16537.4 | 0.11719
31505.7 | 0.018908 | 31098.8 | 0.019213 | 31129.9 | 0.019309 | 30789.4 | 0.019897 | 13822.6 | 0.033391 | 10972.7 | 0.061314 | 9706.68 | 0.074754 | 12757.2 | 0.063422 | 13386.1 | 0.071446 | 12269.7 | 0.11454 | 13626 | 0.11599 | 14629.2 | 0.14061
30089.3 | 0.019406 | 29671 | 0.019582 | 29700.7 | 0.019798 | 29375.8 | 0.020401 | 11760.4 | 0.037551 | 9465.05 | 0.069151 | 8348.95 | 0.087156 | 10953.9 | 0.073186 | 11686.5 | 0.083062 | 10547.4 | 0.1419 | 11659.8 | 0.14577 | 12830.5 | 0.1742
28650.5 | 0.019798 | 28223.9 | 0.019997 | 28280.4 | 0.020198 | 27943.1 | 0.020897 | 10349.9 | 0.041416 | 8071.46 | 0.080118 | 7394.06 | 0.10006 | 9234.72 | 0.087757 | 10267.2 | 0.096843 | 9437.97 | 0.16918 | 10273.1 | 0.17712 | 11408.7 | 0.21129
27225.9 | 0.020198 | 26820.6 | 0.020503 | 26847.4 | 0.020689 | 26500.7 | 0.021511 | 9208.3 | 0.04594 | 6954.4 | 0.093358 | 6507.24 | 0.11686 | 8122.48 | 0.10191 | 8815.96 | 0.1174 | 8368.11 | 0.20474 | 8938.02 | 0.22094 | 10132.8 | 0.26012
25794.7 | 0.020689 | 25385.3 | 0.021001 | 25410.7 | 0.021297 | 25082.5 | 0.0221 | 8220.8 | 0.051251 | 6060.99 | 0.10916 | 5694.07 | 0.13869 | 7115.61 | 0.12005 | 7861.52 | 0.1379 | 7457.88 | 0.24748 | 8085.34 | 0.26072 | 9171.45 | 0.3112
24365.5 | 0.021297 | 23954.8 | 0.021598 | 23978.8 | 0.021902 | 23645.4 | 0.022796 | 7243.12 | 0.058736 | 5174.53 | 0.13301 | 5034.17 | 0.16337 | 6262.19 | 0.14223 | 6742.54 | 0.17261 | 6529.65 | 0.31138 | 7115.61 | 0.32356 | 8183.21 | 0.38422
22923.7 | 0.021815 | 22514.7 | 0.022211 | 22537.3 | 0.022502 | 22201.7 | 0.02349 | 6440.48 | 0.067392 | 4522.71 | 0.15931 | 4443.1 | 0.19568 | 5536.44 | 0.16938 | 5906.73 | 0.21238 | 5930.47 | 0.3668 | 6330.73 | 0.40016 | 7230.68 | 0.48537
21502.5 | 0.022502 | 21097.8 | 0.022887 | 21118.9 | 0.023303 | 20783.7 | 0.0244 | 5756.39 | 0.077412 | 3899.02 | 0.1985 | 3962.07 | 0.23316 | 5048.61 | 0.194 | 5264.23 | 0.25569 | 5498.51 | 0.42037 | 5664.79 | 0.49012 | 6518.44 | 0.59141
20068.9 | 0.023094 | 19651.8 | 0.023584 | 19691.2 | 0.023989 | 19359.2 | 0.025295 | 5130.25 | 0.089997 | 3388.41 | 0.24606 | 3516.97 | 0.28103 | 4322.57 | 0.24705 | 4678.2 | 0.31084 | 4911.66 | 0.51398 | 4965.42 | 0.6252 | 5792.79 | 0.74114
18637.4 | 0.023893 | 18231.8 | 0.0244 | 18250.1 | 0.024893 | 17924.5 | 0.026406 | 4540.89 | 0.10644 | 2997.43 | 0.30086 | 3084.54 | 0.34957 | 3826 | 0.30155 | 4136.03 | 0.38378 | 4460.95 | 0.61455 | 4435.47 | 0.77058 | 5228.17 | 0.89946
17204.5 | 0.024695 | 16796.5 | 0.025295 | 16830.1 | 0.026013 | 16496.8 | 0.027704 | 4107.69 | 0.1229 | 2659.17 | 0.3668 | 2779.11 | 0.41725 | 3347.88 | 0.37509 | 3681.92 | 0.47166 | 3959.8 | 0.76574 | 3916.93 | 0.98184 | 4635.52 | 1.1408
15786.7 | 0.025702 | 15366.2 | 0.026406 | 15396.9 | 0.027101 | 15061.9 | 0.029212 | 3735.03 | 0.14158 | 2355.03 | 0.45235 | 2498.19 | 0.50407 | 3023.3 | 0.44592 | 3338.31 | 0.56395 | 3642.05 | 0.89432 | 3486.88 | 1.2304 | 4176.51 | 1.4061
14356 | 0.026778 | 13931.7 | 0.027594 | 13973.6 | 0.028491 | 13628.6 | 0.030988 | 3260.81 | 0.1747 | 2104.89 | 0.55435 | 2252.11 | 0.60964 | 2691.36 | 0.55023 | 2983.72 | 0.69549 | 3287.07 | 1.0928 | 3086.3 | 1.5686 | 3743.6 | 1.7641
12925.1 | 0.028011 | 12505.5 | 0.029008 | 12543.1 | 0.030102 | 12196.7 | 0.033301 | 2948.04 | 0.20474 | 1853.5 | 0.70028 | 2051.32 | 0.72893 | 2451.4 | 0.65115 | 2706.82 | 0.8426 | 2995.71 | 1.3089 | 2744.3 | 2.0067 | 3405.92 | 2.1705
11497.9 | 0.029506 | 11080.3 | 0.030771 | 11102.5 | 0.032188 | 10774.4 | 0.036183 | 2683.66 | 0.23911 | 1605.24 | 0.92241 | 1915.03 | 0.8292 | 2206.14 | 0.79296 | 2475.39 | 0.99828 | 2654.6 | 1.6678 | 2508.23 | 2.4466 | 3073.95 | 2.7154
10066 | 0.031299 | 9652.07 | 0.032904 | 9681.07 | 0.034799 | 9338.75 | 0.040229 | 2326.87 | 0.30328 | 1364.19 | 1.2698 | 1776.56 | 0.95521 | 1978.6 | 0.97121 | 2254.69 | 1.1984 | 2397.23 | 2.0721 | 2223.9 | 3.2097 | 2755.33 | 3.5319
8629.38 | 0.033501 | 8216.73 | 0.035787 | 8249.67 | 0.038305 | 8999.53 | 0.041371 | 2058.38 | 0.37294 | 1243.99 | 1.5287 | 1621.88 | 1.1474 | 1763.38 | 1.2136 | 2054.84 | 1.4395 | 2184.75 | 2.5423 | 2008.29 | 4.1179 | 2502.49 | 4.4719
7200.66 | 0.036583 | 6788.11 | 0.039829 | 6815.32 | 0.043492 | 8492.41 | 0.043406 | 1842.91 | 0.45287 | 1102.34 | 1.9501 | 1469.68 | 1.398 | 1596.07 | 1.4813 | 1868.42 | 1.746 | 2012.9 | 3.073 | 1801.16 | 5.4241 | 2300.36 | 5.5466
5772.89 | 0.041001 | 5355.76 | 0.046228 | 6660.36 | 0.044282 | 7894.55 | 0.045906 | 1627.46 | 0.56817 | 996.61 | 2.4229 | 1335.58 | 1.7015 | 1422.46 | 1.8659 | 1713.58 | 2.084 | 1850.31 | 3.7423 | 1640.57 | 6.9788 | 2118.2 | 6.8914
4341.3 | 0.048501 | 5223.53 | 0.047021 | 6418.43 | 0.045494 | 7243.99 | 0.04958 | 1462.95 | 0.6935 | 894.845 | 3.0484 | 1204.71 | 2.1129 | 1290.45 | 2.288 | 1576.08 | 2.5047 | 1704.77 | 4.6124 | 1513.25 | 8.9074 | 1963.91 | 8.6213
4251.08 | 0.049087 | 5008.68 | 0.048356 | 6093.2 | 0.047304 | 6707.14 | 0.053228 | 1311.31 | 0.85819 | 795.684 | 4.0108 | 1110.58 | 2.522 | 1189.62 | 2.7061 | 1457.93 | 2.9982 | 1564.38 | 5.7373 | 1419.2 | 11.0353 | 1832.38 | 10.7176
4137.84 | 0.049978 | 4717 | 0.050582 | 5726.89 | 0.04958 | 6081.02 | 0.058474 | 1164 | 1.0748 | 735.619 | 4.8871 | 1004.63 | 3.1424 | 1084.8 | 3.3429 | 1329.47 | 3.7102 | 1438.85 | 7.227 | 1324.91 | 14.1172 | 1715.54 | 13.339
3983.55 | 0.051295 | 4442.3 | 0.05291 | 5350.41 | 0.052488 | 5574.33 | 0.064045 | 1030.28 | 1.3656 | 667.733 | 6.364 | 904.121 | 3.9971 | 989.215 | 4.1845 | 1213.02 | 4.6576 | 1341.71 | 8.8413 | 1258.32 | 17.5601 | 1626.53 | 16.2907
3759.08 | 0.053388 | 4117.2 | 0.056069 | 4939.05 | 0.056182 | 5069.15 | 0.070994 | 922.963 | 1.7035 | 613.8 | 8.1134 | 832.048 | 4.8983 | 915.065 | 5.1075 | 1108.67 | 5.8401 | 1251.85 | 11.029 | 1188.26 | 22.8405 | 1539.48 | 20.4267
3518.99 | 0.056069 | 3831.18 | 0.059596 | 4541.12 | 0.060618 | 4674.74 | 0.078069 | 823.984 | 2.1532 | 561.643 | 10.7237 | 764.405 | 6.0964 | 840.673 | 6.4484 | 1026.16 | 7.2601 | 1174.05 | 13.8529 | 1131.13 | 31.1196 | 1458.77 | 26.6301
3297.53 | 0.058885 | 3501.44 | 0.064431 | 4217.21 | 0.064948 | 4183.6 | 0.089174 | 736.041 | 2.7216 | 524.929 | 13.4002 | 707.917 | 7.5572 | 793.863 | 7.6969 | 945.983 | 9.4055 | 1097.3 | 17.9157 | 1089.78 | 42.1093 | 1405.44 | 33.1624
3083.83 | 0.062215 | 3190.49 | 0.070428 | 3892.97 | 0.070287 | 3858.09 | 0.09875 | 676.203 | 3.2691 | 487.253 | 18.1532 | 668.116 | 8.9329 | 738.575 | 9.6788 | 889.224 | 11.4933 | 1046.34 | 22.3743 | 1054.77 | 57.4057 | 1357.95 | 41.7012
2849.58 | 0.066393 | 2907.15 | 0.07706 | 3666.26 | 0.074933 | 3579.32 | 0.10914 | 603.341 | 4.3011 | 462.765 | 23.2897 | 612.045 | 12.1569 | 687.138 | 12.4958 | 833.479 | 14.3044 | 997.182 | 29.1191 | 1024.39 | 81.7405 | 1320.36 | 55.118
2648.98 | 0.070781 | 2635.76 | 0.085592 | 3459.67 | 0.079965 | 3307.43 | 0.12183 | 559.716 | 5.2199 | 442.541 | 30.1373 | 569.746 | 15.8307 | 638.551 | 16.6778 | 791.139 | 17.37 | 961.28 | 38.1585 | 1003.48 | 119.225 | 1285.28 | 72.6014
2460.03 | 0.075837 | 2416.14 | 0.094499 | 3168.23 | 0.088287 | 2998.68 | 0.14041 | 516.871 | 6.4484 | 425.631 | 40.2693 | 534.335 | 20.8045 | 606.807 | 20.9121 | 747.515 | 22.2976 | 933.064 | 49.5762 | 988.649 | 172.411 | 1261.21 | 94.7039
2300.61 | 0.081092 | 2170.97 | 0.10762 | 2858.15 | 0.099842 | 2784.79 | 0.15737 | 481.15 | 8.0026 | 414.323 | 51.1043 | 501.125 | 28.623 | 572.035 | 28.5903 | 710.355 | 29.0026 | 907.755 | 66.0163 | 979.628 | 263.871 | 1243.27 | 120.667
2132.24 | 0.087671 | 2004.05 | 0.11929 | 2586.16 | 0.11382 | 2534.95 | 0.1832 | 449.439 | 9.824 | 401.701 | 70.3096 | 481.426 | 36.7008 | 552.706 | 35.993 | 685.958 | 36.9328 | 890.243 | 87.6568 | 976.825 | 361.376 | 1227 | 163.655
1990.08 | 0.094594 | 1826.08 | 0.13491 | 2309.83 | 0.1321 | 2309.83 | 0.21221 | 419.098 | 12.4458 | 393.05 | 92.9306 | 473.493 | 41.749 | 531.587 | 52.7701 | 660.504 | 51.2802 | 878.589 | 117.597 | 974.589 | 495.762 | 1217.2 | 216.061
1806.1 | 0.1057 | 1699.23 | 0.1488 | 2081.67 | 0.15364 | 2100.49 | 0.24928 | 393.952 | 15.858 | 385.91 | 126.181 | 459.331 | 55.4663 | 520.437 | 66.6241 | 647.392 | 66.0163 | 869.077 | 152.26 | 975.148 | 595.832 | 1210.24 | 302.41
1640.78 | 0.11894 | 1592.29 | 0.16281 | 1896.81 | 0.17655 | 1937.06 | 0.28732 | 373.725 | 20.345 | 380.422 | 168.41 | 448.925 | 75.0538 | 511.275 | 86.9069 | 633.45 | 89.7397 | 863.618 | 210.684 |  |  | 1206.09 | 413.919
1471.34 | 0.13667 | 1468.4 | 0.18412 | 1719.74 | 0.20491 | 1777.44 | 0.33482 | 359.858 | 25.6128 | 377.383 | 218.675 | 439.509 | 104.09 | 503.139 | 112.781 | 623.012 | 116.591 | 860.654 | 279.907 |  |  | 1202.64 | 540.549
1333.99 | 0.1569 | 1358.22 | 0.20739 | 1584.35 | 0.2336 | 1629.34 | 0.39174 | 348.096 | 33.1624 | 375.012 | 281.676 | 434.252 | 141.821 | 499.12 | 148.301 | 615.914 | 160.591 | 856.718 | 364.703 |  |  | 1204.02 | 595.832
1224.06 | 0.17672 | 1241.32 | 0.23903 | 1447.98 | 0.27059 | 1492.08 | 0.45925 | 337.685 | 43.2087 | 373.297 | 358.901 | 431.277 | 184.89 | 496.553 | 192.124 | 613.097 | 202.056 | 855.247 | 449.249
1140.16 | 0.19688 | 1160.87 | 0.26709 | 1326.01 | 0.31375 | 1342.01 | 0.56093 | 329.657 | 55.4346 | 370.527 | 478.465 | 430.043 | 256.275 | 494.282 | 243.538 | 609.944 | 275.454 | 856.228 | 547.404
1049.35 | 0.22309 | 1079.15 | 0.30054 | 1193.84 | 0.376 | 1222.83 | 0.66887 | 322.557 | 73.0184 | 370.103 | 558.169 | 430.043 | 353.393 | 493.15 | 312.984 | 607.851 | 382.241 | 855.737 | 599.942
958.08 | 0.25739 | 992.206 | 0.34675 | 1103.15 | 0.43337 | 1087.82 | 0.82931 | 317.97 | 91.5045 | 369.256 | 600.629 | 429.059 | 453.645 | 492.586 | 412.262 | 607.155 | 479.014
869.511 | 0.30175 | 912.265 | 0.40125 | 1010.22 | 0.50704 | 991.214 | 0.99585 | 313.987 | 120.322 |  |  | 428.813 | 553.394 | 491.458 | 506.671 | 605.765 | 571.432
809.916 | 0.33954 | 829.589 | 0.47561 | 922.356 | 0.5974 | 904.092 | 1.1934 | 310.232 | 160.683 |  |  | 428.568 | 599.942 | 490.052 | 598.226 | 606.46 | 596.515
740.948 | 0.39488 | 767.341 | 0.54653 | 862.583 | 0.67763 | 812.35 | 1.4901 | 307.93 | 205.911
673.125 | 0.46666 | 699.895 | 0.64781 | 804.267 | 0.77634 | 743.175 | 1.7929 | 305.996 | 269.523
619.511 | 0.53947 | 625.738 | 0.7952 | 748.395 | 0.8939 | 678.532 | 2.1833 | 305.121 | 357.874
575.898 | 0.61498 | 558.878 | 0.9889 | 697.799 | 1.0272 | 632.026 | 2.5494 | 304.074 | 437.316
527.913 | 0.72097 | 510.265 | 1.1804 | 648.026 | 1.1887 | 582.851 | 3.043 | 303.204 | 532.559
492.715 | 0.81942 | 468.685 | 1.3991 | 606.031 | 1.3605 | 542.361 | 3.5961 | 303.03 | 602.697
458.487 | 0.93879 | 427.063 | 1.697 | 569.029 | 1.5556 | 508.737 | 4.1864
420.284 | 1.1127 | 393.441 | 2.0114 | 534.82 | 1.7733 | 475.293 | 4.9374
384.495 | 1.3229 | 362.104 | 2.3985 | 501.163 | 2.0418 | 443.16 | 5.9112
349.999 | 1.5965 | 332.264 | 2.9033 | 466.814 | 2.3937 | 416.519 | 7.0206
323.737 | 1.8811 | 306.412 | 3.4968 | 442.717 | 2.6962 | 387.583 | 8.5493
306.106 | 2.1124 | 284.556 | 4.1655 | 419.025 | 3.0705 | 367.209 | 10.0527
283.42 | 2.4715 | 269.328 | 4.7628 | 398.191 | 3.4724 | 346.863 | 12.0956
260.586 | 2.9708 | 255.681 | 5.4349 | 379.15 | 3.9151 | 328.63 | 14.5246
240.07 | 3.571 | 244.186 | 6.2205 | 363.555 | 4.3312 | 315.113 | 17.1302
222.723 | 4.2369 | 231.813 | 7.2634 | 348.602 | 4.8348 | 303.06 | 20.0022
208.498 | 5.002 | 221.391 | 8.4052 | 333.93 | 5.4349 | 289.146 | 25.3263
195.182 | 5.8994 | 212.285 | 9.6973 | 321.157 | 6.0729 | 277.253 | 31.4641
184.737 | 6.8404 | 203.35 | 11.2441 | 304.579 | 7.0276 | 267.717 | 38.2386
174.501 | 8.0032 | 195.572 | 13.0116 | 293.222 | 7.8291 | 259.805 | 46.5649
168.331 | 8.8715 | 188.846 | 15.0721 | 282.289 | 8.792 | 251.371 | 58.724
162.216 | 9.8833 | 182.168 | 17.6696 | 272.307 | 9.9726 | 243.698 | 76.161
157.108 | 10.9994 | 175.903 | 20.8394 | 261.368 | 11.5057 | 236.733 | 99.968
151.249 | 12.8051 | 170.533 | 24.5778 | 250.618 | 13.3811 | 231.581 | 128.747
146.633 | 14.6852 | 166.656 | 28.4414 | 243.211 | 15.057 | 227.223 | 166.143
140.18 | 17.9725 | 162.379 | 34.3928 | 236.969 | 17.0107 | 223.84 | 214.831
136.31 | 20.632 | 159.641 | 40.1992 | 229.736 | 19.6454 | 220.287 | 283.965
131.885 | 24.5042 | 157.108 | 47.4581 | 223.616 | 22.6202 | 216.79 | 386.778
128.243 | 28.958 | 154.305 | 57.3314 | 217.877 | 26.2547 | 214.848 | 502.629
125.202 | 34.1187 | 152.008 | 69.2587 | 213.136 | 30.2909 | 214.419 | 599.954
122.6 | 40.0788 | 150.345 | 82.8349 | 208.707 | 35.0174
120.413 | 47.0329 | 148.551 | 104.256 | 204.37 | 40.8476
118.147 | 57.5612 | 146.633 | 130.823 | 200.323 | 47.696
116.504 | 68.8444 | 144.884 | 181.971 | 196.749 | 56.8746
114.77 | 82.0927 | 143.012 | 254.131 | 193.433 | 67.8873
113.174 | 99.868 | 141.873 | 339.289 | 190.172 | 81.1946
111.936 | 126.83 | 140.883 | 471.94 | 186.78 | 99.968
110.933 | 172.405 | 140.321 | 585.141 | 183.999 | 121.007
110.38 | 220.269 | 140.18 | 599.954 | 181.26 | 154.447
109.72 | 279.737 |  |  | 179.098 | 188.642
109.173 | 342.014 |  |  | 176.431 | 239.332
108.737 | 445.346 |  |  | 174.85 | 290.281
108.628 | 574.128 |  |  | 172.592 | 391.448
108.628 | 599.954 |  |  | 171.388 | 540.153
|  |  |  | 171.046 | 599.954