## 400_7MM
S&C Fault Fiter Electronic Power Fuses
Instantaneous-Curve-Type Control Module (TCC 400-7)
Total Clearing Time-Current Characteristic Curve Dated September 8, 1986
Tolerance: Curves are plotted to maximum test points. All variations are minus
5 kA |  | 6 kA |  | 8 kA |  | 10 kA |  | 12 kA
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
6801.7 | 0.01 | 8282.73 | 0.01 | 12245.6 | 0.01 | 17781.7 | 0.01 | 24147.2 | 0.01
6801.7 | 0.016307 | 8282.73 | 0.015574 | 12245.6 | 0.015512 | 17710.7 | 0.012374 | 24147.2 | 0.016
6801.7 | 0.02349 | 8282.73 | 0.024013 | 12233.4 | 0.021064 | 17657.7 | 0.017542 | 24099 | 0.023514
6761.01 | 0.025728 | 8110.61 | 0.025447 | 12039.2 | 0.023917 | 17587.2 | 0.022614 | 23386.8 | 0.02423
6667.02 | 0.029654 | 7997.85 | 0.028321 | 11636.8 | 0.024968 | 17152.9 | 0.024206 | 22786.5 | 0.028922
6561.2 | 0.034042 | 7855.18 | 0.031519 | 11486.5 | 0.026222 | 16729.4 | 0.027566 | 22650.2 | 0.029862
6412.01 | 0.034695 | 7777.02 | 0.032479 | 11236.5 | 0.029773 | 16463.9 | 0.030957 | 17710.7 | 0.031963
6303.93 | 0.035502 | 7457.15 | 0.034487 | 11080.3 | 0.03222 | 14897.1 | 0.031836 | 16283.8 | 0.032609
6303.93 | 0.039275 | 7346.12 | 0.035502 | 10320.9 | 0.034938 | 12989.9 | 0.033036 | 15551.7 | 0.033102
6303.93 | 0.14512 | 7346.12 | 0.082979 | 9817.56 | 0.03536 | 11967.2 | 0.03394 | 15182.9 | 0.039236
6303.93 | 1.2471 | 7346.12 | 0.99884 | 9366.81 | 0.035859 | 11636.8 | 0.04096 | 14837.7 | 0.047304
6303.93 | 98.0865 | 7346.12 | 57.2168 | 9385.56 | 0.054521 | 11326.8 | 0.049829 | 14428 | 0.048744
6303.93 | 945.633 | 7346.12 | 1000.1 | 9385.56 | 0.76862 | 11338.1 | 0.056407 | 13959.6 | 0.060255
6303.93 | 1000.1 |  |  | 9385.56 | 54.7539 | 11338.1 | 0.075008 | 13601.3 | 0.078303
|  |  |  | 9385.56 | 609.631 | 11304.1 | 0.095163 | 13560.6 | 0.094028
|  |  |  | 9385.56 | 1006.11 | 11304.1 | 0.21824 | 13560.6 | 0.85713
[6 empty] | 11304.1 | 0.4896 | 13560.6 | 102.703
[6 empty] | 11304.1 | 2.0747 | 13560.6 | 1000.1
[6 empty] | 11304.1 | 49.5929
[6 empty] | 11304.1 | 514.838
[6 empty] | 11304.1 | 1000.1